## Proposed Curve
There is one reserve curve per reserve product i.e. FFR curve, POR curve, etc.
Maximum Output
GMX | 100
Reserve Curve Values
RMX | 10
GMN | 10
R0 | 0
R1 | 7
R2 | 5
Δ1 | 0
Δ2 | 5
Δ3 | 10
β | 10
MW Curve Points
GMN+β | 20
GMX-Δ3 | 90
GMX-Δ2 | 95
GMX-Δ1 | 100
Input Variables
Declared Reserve | 10
Current Output | 50
Available Reserve | 10
Ruleset for Calculating the Reserve Curve
|  | GMN | Minimum Load (IE) / Minimum Generation (NI)
|  | GMX | Maximum Output
|  | RMX | Maximum reserve volume (shall be provided across the full range between GMN+β to GMX-Δ3)
|  | R0 | Reserve volume provided at GMX (Normally 0 MW)
|  | Δ1 | 0 if the unit will provide reserve at any load point < GMX.
|  | R2 | Reserve provided at GMX-Δ2 (R2 is normally ≤ Δ2)
|  | R1 | Reserve provided at GMN
Δ3 ≥ Δ2 > Δ1
RMX ≥ R2 > R0
Suggested Methodology for Units with Ambient Declarations*
1. Set GMX = maximum availability at the time of testing
2. Calculate the values for Δ1, Δ2, Δ3, R0, R2, RMX using that value for GMX
3. Set GMX = Registered Capacity / MCR
For the purpose of the contract, GMX is Registered Capacity (or MCR). For the purpose of monitoring, GMX is the declared availability.
*This may not reflect the unit's actual capability. The contracting unit shall decide whether this approach is suitable for their unit or not.

## Graph Calculations (hidden)
Curve Workings
|  | Scenario 5 | Scenario 4 | Scenario 3 | Scenario 2 | Scenario 1 |  |  |  | Scenario 5 | Scenario 4 | Scenario 3 | Scenario 2 | Scenario 1 |  | RANGE | RESERVE
x point |  | 0 | 0 | 0 | 0 | 1 |  | y point |  | 0 | 0 | 0 | 0 | 1
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GMN | 10 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GMN | 10 | 0 | 0 | 0 | 0 | 10 | 10 | R1 | 7 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 0
GMN+β | 20 | 0 | 0 | 0 | 0 | 20 | 20 | RMX | 10 | 0 | 0 | 0 | 0 | 10 | 10 | 1 | 10
GMX-Δ3 | 90 | 0 | 0 | 0 | 0 | 90 | 90 | RMX | 10 | 0 | 0 | 0 | 0 | 10 | 10 | 0 | 0
GMX-Δ2 | 95 | 0 | 0 | 0 | 0 | 95 | 95 | R2 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0
RD2_x (R0) | 100 | 0 | 0 | 0 | 0 | 100 | 100 | R0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GMX | 100 | 0 | 0 | 0 | 0 | 100 | 100 | R0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Detailed Range / Reserve
Scenario 1 |  |  | In Range? | Reserve | Scenario 2 |  |  | In Range? | Reserve | Scenario 3 |  |  | In Range? | Reserve | Scenario 4 |  |  | In Range? | Reserve | Scenario 5 | In Range? | Reserve
MW < GMN |  |  | 0 | 0 | MW < GMN |  |  | 0 | 0 | MW < GMN |  |  | 0 | 0 | MW < GMN |  |  | 0 | 0 | MW < GMN | 0 | 0
GMN ≤ MW < GMN+β |  |  | 0 | 0 | GMN ≤ MW < IN1_x |  |  | 0 | 0 | GMN ≤ MW < IN2_x |  |  | 0 | 0 | GMN ≤ MW < RU_x (R0) |  |  | 0 | 0 | GMN ≤ MW < GMX | 0 | 0
GMN+β ≤ MW < GMX-Δ3 |  |  | 1 | 10
GMX-Δ3 ≤ MW < GMX-Δ2 |  |  | 0 | 0 | (IN1_x ¦ GMN) ≤ MW < GMX-Δ2 |  |  | 0 | 0
GMX-Δ2 ≤ MW < RD2_x (R0) |  |  | 0 | 0 | GMX-Δ2 ≤ MW < RD2_x (R0) |  |  | 0 | 0 | (IN2_x ¦ GMN) <= MW < RD2_x (R0) |  |  | 0 | 0
RD2_x (R0) ≤ MW ≤ GMX |  |  | 0 | 0 | RD2_x (R0) ≤ MW ≤ GMX |  |  | 0 | 0 | RD2_x (R0) ≤ MW ≤ GMX |  |  | 0 | 0 | (RU_x (R0) ¦ GMN) ≤ MW ≤ GMX |  |  | 0 | 0
GMX < MW |  |  | 0 | 0 | GMX < MW |  |  | 0 | 0 | GMX < MW |  |  | 0 | 0 | GMX < MW |  |  | 0 | 0 | GMX < MW | 0 | 0
GRAPH DATA | [6 empty] | Sample Input Values | [7 empty] | GMN+β |  | 20
RU | [7 empty] | PBC | TB3 | AD2 | TH1 |  |  |  | GMX-Δ3 |  | 90
0 |  | RU_y (0) |  | 0 | 4 |  | GMX | 463 | 243 | 432 | 73 |  |  |  | GMX-Δ2 |  | 95
GMN |  | R1 |  | 10 | 7 |  | RMX | 60 | 12 | 13 | 68 |  |  |  | GMX-Δ1 |  | 100
GMN+β |  | RMX |  | 20 | 10 |  | GMN | 232 | 121 | 216 | 5 |  |  |  | RU_m |  | 0.3
RU_x (1.2*RMX) |  | 1.2*RMX |  | 26.6667 | 12 |  | R0 | 0 | 0 | 0 | 0 |  |  |  | RU_c |  | 4
RD1 | [6 empty] | R1 | 50 | 0 | 0 | 0 |  |  |  | RU_x (R0) |  | -13.3333
RD1_x (1.2*RMX) |  | 1.2*RMX |  | 88 | 12 |  | R2 | 60 | 12 | 13 | 68 |  |  |  | RU_y (GMX) |  | 34
GMX-Δ3 |  | RMX |  | 90 | 10 |  | β | 48 | 0 | 0 | 0 |  |  |  | RD1_m |  | -1
GMX-Δ2 |  | R2 |  | 95 | 5 |  | Δ1 | 0 | 12 | 0 | 0 |  |  |  | RD1_c |  | 100
1.2*GMX |  | RD1_y (1.2*GMX) |  | 120 | -20 |  | Δ2 | 90 | 24 | 13 | 68 |  |  |  | RD1_y (GMN) |  | 90
RD2 | [6 empty] | Δ3 | 90 | 24 | 13 | 68 |  |  |  | RD2_m |  | -1
RD2_x (1.2*RMX) |  | 1.2*RMX |  | 88 | 12 | [9 empty] | RD2_c |  | 100
GMX-Δ2 |  | R2 |  | 95 | 5 | [9 empty] | RD2_x (R0) |  | 100
RD2_x (R0) |  | R0 |  | 100 | 0 | [9 empty] | RD2_y (GMN) |  | 90
GMX-Δ1 |  | 0 |  | 100 | 0 | [9 empty] | IN1_x |  | 73.8462
IN1 | [14 empty] | IN1_y |  | 26.1538
IN1_x |  | 0 |  | 73.8462 | 0 | [9 empty] | IN2_x |  | 73.8462
IN1_x |  | IN1_y |  | 73.8462 | 12 | [9 empty] | IN2_y |  | 26.1538
IN1_x |  | 1.2*IN1_y |  | 73.8462 | 14.4
IN2
IN2_x |  | 0 |  | 73.8462 | 0
IN2_x |  | IN2_y |  | 73.8462 | 12
IN2_x |  | 1.2*IN2_y |  | 73.8462 | 14.4
Declared Reserve
GMN |  | PDR |  | 10 | 10
GMX |  | PDR |  | 100 | 10