## Cover Sheet
Signal List WINDFARM NAME (TLC) Type A XX MW v1.0 and Control System Parameter Settings
Disclaimer:
This Signal List contains information (and/or attachments) which may be privileged or confidential. All content is intended solely for the use of the individual or entity to whom it is addressed. If you are not the intended recipient please be aware that any disclosure, copying, distribution or use of the contents of this message is prohibited. If you suspect that you have received this Signal List in error please notify EirGrid immediately. Further information can be found at: http://www.eirgridgroup.com/legal/

## Version Control
WINDFARM NAME (TLC) Signal List Version Control
Version | Date | Written by: | Reviewed by: | Approved by: | Description of changes | Change requested by
0.1 |  |  |  |  | first draft
0.2 | 2015-03-23 |  |  |  | Frequency Response updated to clarify performance below DMOL per feedback from industry
0.3 | 2015-06-08 |  |  |  | Recommended Protection Settings updated to reflect ROCOF changes
0.4 | 2016-05-06 |  |  |  | Polarity on the Analogue signals inlcuded within ETIE Row 2.
0.5 | 2016-10-04 |  |  |  | updated company logo and schedule of tests.
0.6 | 2017-10-01 |  |  |  | Turbine Protection Settings Tab updated to include FRT
0.7 | 2017-03-24 |  |  |  | Addion of Note in Post Ener Pre Grid Code Cert Sheet
1 | 2017-10-02 | Neil Kavanagh |  |  | Adding in system services
1.1 |  | Claire Delaney |  |  | Adding in request for met mast height, clarifying system services details, reactive device status on/off.
Note on D3: Administrator: All signal lists circulated to EMS and ESBT for Review before issuance.

## Signal Specification
TSO Remote Control Enable Switch (RCES)
RCES shall block all commands from the TSO RTU to the WFPS, including set-point enable pulses (except for the Blue Alert Lamp indication in TSO WFs following a Black Start Shutdown Command)
Turning the RCES ON or OFF shall not impact/change the status of any signals, commands, set-points or control modes (other than the position indication of the RCES).
For TSO WFPS
Blackstart Shutdown
See the "Blackstart Shutdown" tab for details on the functionality of Blackstart Shutdown.
Blackstart Shutdown feedback is provided from the associated transmission station, not from the WFPS
For DSO WFPS
Dispatch Fail Lamp
Dispatch Fail Lamp ON command shall turn on indication lamp in WFPS control room unless TSO RCES is OFF
Dispatch Fail Lamp OFF command shall turn off indication lamp in WFPS control room unless TSO RCES is OFF
Blue Alert Lamp
TSO WF: Black Start Shutdown ON command shall turn on Blue Alert indication lamp in WFPS control room
TSO WF: Black Start Shutdown OFF command shall turn off Blue Alert indication lamp in WFPS control room
DSO WF: Blue Alert Lamp ON command shall turn on indication lamp in WFPS control room unless TSO RCES is OFF
DSO WF: Blue Alert Lamp OFF command shall turn off indication lamp in WFPS control room unless TSO RCES is OFF
Set-point Enable Pulse
When a WFPS receives a set-point enable pulse (e.g. Active Power Control Set-point Enable), it shall implement the set-point on the associated analogue input (e.g. implement the Active Power Control set-point being received at that time).
If an analogue set-point signal changes and a corresponding set-point enable pulse is not issued, the WFPS shall ignore the change in the analogue signal.
Feedback for Analogue Signals
Feedback for analogue signals shall reflect the last received valid signal
i.e. feedback signals should not be looped from the analogue input. They should only change value when an Enable Pulse is received, and should not change value when the corresponding mode (e.g. Active Power Control) is turned off or the Remote Control Enable Switch is turned off.
Active Power Control ON/OFF
When Active Power Control is turned off, the set-point feedback shall not change, but wind farm output shall increase to maximum available MW.
Set-points received while Active Power Control is OFF should be ignored.
Active Power Control Set-point (Feedback)
The Active Power Control set-point feedback should not change when APC is switched on or off. It should reflect the last valid set-point that the WFPS received from NCC.
Note. Locally implemented set-points should not be fed back to NCC.
Worked Example:
● NCC turns APC on and issues a set-point of 10 MW (feedback goes to 10 MW, WFPS implements 10 MW set-point)
● NCC issues a set-point of 8 MW (feedback goes to 8 MW, WFPS implements 8 MW set-point)
● NCC turns APC off (feedback remains at 8 MW, WFPS ramps to minimum of AAP and Registered Capacity)
● NCC issues a set-point of 5 MW (feedback remains at 8 MW, WFPS remains at minimum of AAP and Registered Capacity)
● NCC turns APC on (feedback remains at 8 MW, WFPS ramps to 8 MW)
● NCC issues a set-point of Registered Capacity and turns APC off (feedback goes to Registered Capacity, WFPS ramps to minimum of AAP and Registered Capacity)
If the WFPS is reset, the default settings for the various controls should commit current state to memory (if this is not possible, default should be APC off, FQR on, Curve 1 etc.)
Frequency Response ON/OFF
When Frequency Response is Off, the WFPS shall not respond to any changes in Frequency. When Frequency Response is On, the WFPS shall respond to frequency in line with the specified frequency response settings.
When Frequency Response is turned On or Off, the selected Frequency Curve (and feedback) shall not be affected. i.e. Curve signal does not go suspect, and does not reset to a default value.
If Frequency Response is OFF, the Curve should not change.
Frequency Droop
Droop set-points received while Frequency Response is OFF should be ignored.
Frequency Droop must be settable in the range 2% to 10%, per Grid Code V7 clause PPM1.5.3.1
WFPS should treat any set-point <= 2% as 2% (implement 2% and provide 2% feedback)
WFPS should treat any set-point >= 10% as 10% (implement as 10% and provide 10% feedback)
Frequency Droop signal is specified in the range 0% to 12%, to facilitate signals at the upper and lower ends of the scale
In the case of hardware/software update or reset, the existing value shall be maintained. In the case that the existing value is lost, the WFPS shall default to 4%.
This signal shall be implemented in increments of 0.1% i.e. to 1 decimal place.
For TSO WFPS or DSO Type A or B WFPS
Reactive Power Control Modes (kV, Mvar, PF)
One control mode will be ON (in operation) at all time: Voltage Control (kV), Mvar Control (Q), or Power Factor Control (PF).
There are no individual OFF commands. NCC will toggle between control modes by sending an ON command for the required mode.
Position indication for the mode in operation will indicate ON and position indication for the other two modes will indicate OFF.
Response time to a change in set-point: as per Grid Code V7 clause PPM1.6.2.2
Power Factor Set-points:
Power Factor set-points are issued as an angle (±90 degrees), to avoid the signalling difficulties associated with issuing the non-linear Power Factor set-points.
If a positive angle is issued, the Power Factor implemented by the controll will be positive. If a negative angle is issued, the Power Factor implemented by the controller will be negative.
Worked Examples:
1) NCC issues A set-point of +18.19 degrees, WFPS implements a set-point of +cos(18.19) = +0.95 PF
2) NCC issues A set-point of -18.19 degrees, WFPS implements a set-point of -cos(18.19) = -0.95 PF
3) NCC issues A set-point of 0 degrees, WFPS implements a set-point of cos(0) = 1 PF
4) A WFPS exporting 100 MW with a set-point of +18.19 degrees would export +32.85 Mvar. i.e. Tan(+18.19)*100
Changing Control Modes (Bumpless Transfer):
1. WFPS calculates a set-point which will cause no change in Mvar. 2. WFPS continues to regulate to calculated set-point in the new mode.
Worked Example:
A WFPS with a Registered Capacity of 100 MW is exporting 50 MW, operating at a voltage slope setting of 4%. System voltage Is 118 kV and the kV set-point is 115 kV, therefore the WFPS is absorbing its maximum leading capability of 32.9 Mvar.
● NCC issues Mvar (Q) Control ON.
● WFPS calculates and implements a Mvar set-point of 32.9 Mvar, consistent with the current Mvar output. WFPS returns Mvar (Q) Control feedback ON, Voltage (kV) Control feedback OFF and Power Factor (PF) Control feedback OFF. Set-point feedback signals do not change.
● NCC issues a Mvar set-point of 10 Mvar.
● TSO RTU issues a Mvar (Q) Control set-point enable pulse to the WFPS. WFPS returns a set-point feedback of 10 Mvar and implements the set-point of 10 Mvar.
● NCC issues Power Factor (PF) Control ON.
● WFPS calculates and implements a Power Factor set-point of +0.98, consistent with the current MW and Mvar output. WFPS returns Power Factor (PF) Control feebdack ON, Voltage (kV) Control feedback OFF and Mvar (Q) Control feedback OFF. Set-point feedback signals do not change.
● NCC issues a Power Factor set-point of 0 degrees.
● TSO RTU issues a Power Factor (PF) set-point enable pulse to the WFPS. WFPS returns a set-point feedback of 0 degrees and implements the set-point of 0 degrees (1 PF).
● NCC issues Voltage (kV) Control ON.
● WFPS calculates and implements a Voltage set-point of 118 kV, consistent with the current system voltage and Mvar output. WFPS returns Voltage (kV) Control feebdack ON, Power Factor (PF) Control feedback OFF and Mvar (Q) Control feedback OFF. Set-point feedback signals do not change.
● NCC issues a Voltage set-point of 115 kV.
● TSO RTU issues a Voltage (kV) set-point enable pulse to the WFPS. WFPS returns a set-point feedback of 115 kV and implements the set-point of 115 kV.
Available Active Power
AAP must reflect what the WFPS is capable of exporting at that point in time
While a WTG is Shut down for maintenance, fault, high or low wind speed Shut down, flicker or noise, that turbine shall not be included in AAP
While a the output of a WTG is reduced due to Active Power Control Set-Point or frequency response, AAP shall reflect what the WFPS would be exporting if that APC set-point was not in place (accounting for WTGs that are shut down for reasons, above)
AAP shall not be greater than MEC.
% Availability
Specified in Grid Code and signal list as 0-100%
Grid Code definition of Controllable WFPS Availability: The amount of MW the Controllable WFPS can produce given favourable wind conditions
i.e. The combined capacity of all WTGs in service (including WTGs shut down due to APC set-point, or high/low wind speed shutdown) as a percentage of installed capacity.
This signal is independent of wind conditions and high or low wind speed shutdown.
Note. Any WTG which is stopped or shut down (not due to APC set-point, or high/low wind speed shutdown) should reduce the % Availability accordingly.
Worked examples:
1) Wind farm with 10 * 1 MW turbines
● Registered Capacity = 10 MW
● Out Of Service: 2 * 1 MW
2) Wind farm with 5*1 MW turbines and 5*2 MW turbines
● Registered Capacity = 15 MW
● Out of service: 1*1 MW turbine and 2*2 MW turbines
3) Wind farm with 20*1 MW turbines with an MEC of 18 MW
● Registered Capacity = 18 MW
● Out of service: 2 * 1 MW Turbines
% High Wind Speed Shutdown
% of installed MW that is shut down due to high wind speed
Worked example:
● Wind farm with 5*1 MW turbines and 5*2 MW turbines (15 MW total installed capacity) with an MEC of 13 MW
● Registered Capacity = 13 MW
● Out of service: 1*1 MW turbine and 2*2 MW turbines
● Shut down due to high wind speed: 1*1 MW turbine and 1*2 MW turbine
% Low Wind Speed Shutdown
% of installed MW that is shut down due to low wind speed
Worked example:
● Wind farm with 5*1 MW turbines and 5*2 MW turbines (15 MW total installed capacity) with an MEC of 13 MW
● Registered Capacity = 13 MW
● Out of service: 3*2 MW turbines
● Shut down due to low wind speed: 3*1 MW turbines
Emulated Inertia
Emulated Inertia FFR Availability
Defined in the "DS3 System Services New Signals Requirements for the Regulated Arrangements"
Emulated Inertia POR Availability
Defined in the "DS3 System Services New Signals Requirements for the Regulated Arrangements"
Transformer Tap Position
Transformer tap position is indicated via a 0-10 mA analogue signal. The lowest tap will be enumerated as 1 in the EirGrid EMS.
Worked Example:
1) A transformer tap range of -13 to +13 is represented as tap 1 to 27.
2) A transformer tap range of -13 to +7 is represented as tap 1 to 21.
Post Energisation
During Post energisation signals testing there should be NO external influencing factors, e.g. no commissioning works should take place on any turbines on site, as this may influence the outcome of the test.
% 𝐻𝑖𝑔ℎ 𝑊𝑖𝑛𝑑 𝑆𝑝𝑒𝑒𝑑 𝑆ℎ𝑢𝑡𝑑𝑜𝑤𝑛= (1∗1 𝑀𝑊+1∗2 𝑀𝑊)/(15 𝑀𝑊)∗100=20%
% 𝐴𝑣𝑎𝑖𝑙𝑎𝑏𝑖𝑙𝑖𝑡𝑦= (10 𝑀𝑊−(2∗1 𝑀𝑊))/(10 𝑀𝑊)∗100=80%
% 𝐴𝑣𝑎𝑖𝑙𝑎𝑏𝑖𝑙𝑖𝑡𝑦= (15 𝑀𝑊−(1∗1 𝑀𝑊+2∗2 𝑀𝑊))/(15 𝑀𝑊)∗100=66.666%
% 𝐴𝑣𝑎𝑖𝑙𝑎𝑏𝑖𝑙𝑖𝑡𝑦= (20 𝑀𝑊−(2∗1 𝑀𝑊))/(20 𝑀𝑊)∗100=90%
% 𝐴𝑣𝑎𝑖𝑙𝑎𝑏𝑖𝑙𝑖𝑡𝑦= (𝐼𝑛𝑠𝑡𝑎𝑙𝑙𝑒𝑑 𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦 −𝑐𝑎𝑝𝑎𝑐𝑖𝑡𝑦 𝑜𝑓 𝑊𝑇𝐺𝑠 𝑛𝑜𝑡 𝑖𝑛 𝑠𝑒𝑟𝑣𝑖𝑐𝑒 (𝑒.𝑔. 𝑢𝑛𝑑𝑒𝑟 𝑚𝑎𝑖𝑛𝑡𝑒𝑛𝑎𝑛𝑐𝑒 𝑜𝑟 𝑓𝑎𝑢𝑙𝑡))/(𝐼𝑛𝑠𝑡𝑎𝑙𝑙𝑒𝑑 𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦)∗100
% 𝐻𝑖𝑔ℎ 𝑊𝑖𝑛𝑑 𝑆𝑝𝑒𝑒𝑑 𝑆ℎ𝑢𝑡𝑑𝑜𝑤𝑛= (𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦 𝑜𝑓 𝑊𝑇𝐺𝑠 𝑖𝑛 𝐻𝑖𝑔ℎ 𝑊𝑖𝑛𝑑 𝑆𝑝𝑒𝑒𝑑 𝑆ℎ𝑢𝑡𝑑𝑜𝑤𝑛)/(𝐼𝑛𝑠𝑡𝑎𝑙𝑙𝑒𝑑 𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦)∗100
% 𝐿𝑜𝑤 𝑊𝑖𝑛𝑑 𝑆𝑝𝑒𝑒𝑑 𝑆ℎ𝑢𝑡𝑑𝑜𝑤𝑛= (𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦 𝑜𝑓 𝑊𝑇𝐺𝑠 𝑖𝑛 𝐿𝑜𝑤 𝑊𝑖𝑛𝑑 𝑆𝑝𝑒𝑒𝑑 𝑆ℎ𝑢𝑡𝑑𝑜𝑤𝑛)/(𝐼𝑛𝑠𝑡𝑎𝑙𝑙𝑒𝑑 𝐶𝑎𝑝𝑎𝑐𝑖𝑡𝑦)∗100
% 𝐿𝑜𝑤 𝑊𝑖𝑛𝑑 𝑆𝑝𝑒𝑒𝑑 𝑆ℎ𝑢𝑡𝑑𝑜𝑤𝑛= (3∗1 𝑀𝑊)/(15 𝑀𝑊)∗100=20%
M𝑣𝑎𝑟= 𝑇𝑎𝑛(𝑠𝑒𝑡𝑝𝑜𝑖𝑛𝑡)∗𝑀𝑊 𝑂𝑢𝑡𝑝𝑢𝑡

## DSO Required Inputs
WFPS Inputs for Signal List Development
1 | Wind Farm Power Station (WFPS) Name (including alternative names) | Included in submission 
2 | WFPS Connection Type as per the Distribution Code DCC11.1.4 | Included in submission 
3 | WFPS Maximum Export Capacity | Included in submission 
4 | WFPS Installed Capacity (for Phase developments, i.e. MEC 20MW Phase 1 10MWQ1 2014, Phase 2 additional 10MW Q2 2015 ) | Included in submission 
5 | The number of Market Units at the WFPS (Phase 1 &2 is one market unit or two separate market units, noting that if the WFPS consists of two market units then additional signals will be required). | Included in submission 
6 | Turbine Manufacturer | Included in submission 
7 | Tubrine Procurement Date | Included in submission 
8 | Turbine Design Minimum Operating Level | Included in submission 
9 | Energisation Date | Included in submission 
10 | Single Line Diagram (Note that for changes in SLD's, the Signal list requirements may change) | Included in submission 
| · Revision Number | Included in submission 
| · Ownership boundaries | Included in submission 
| · HV CB positions (WFPS and ESBN as applicable) | Included in submission 
| · MV CB positions | Included in submission 
| · MV Feeders | Included in submission 
11 | Grid Connected Transformer tap range | Included in submission 
12 | Number of and Height of Met Mast on site - (if WFPS ≥10MW) | Included in submission 
13 | Nearest 110kV Station - normal feeding arrangements for WFPS | Included in submission 
14 | Confirmation of DSO RTU for the WFPS? | Included in submission 
15 | If there is no DSO RTU submission of DCC signals to be included within the DSO RTU (1-18). | Included in submission 
16 | System Services Provided | Fast Frequency Response:  Primary Operating Reserve:  Secondary Operating Reserve:  Tertiary Operating Reserve:  Steady-State Reactive Power: 
Information to be submitted to generator_testing@eirgrid.com via NDCC/SDCC

## 0) Signal List
WINDFARM NAME (TLC) |  | Type | A | XX | MW | v1.0 |  | Signals List is based on this Single Line Diagram (SLD) as inserted.
EirGrid Signals, Command & Control Specification
Signals List |  | Registered Capacity: XX MW |  |  | Installed Plant: XXX MW |  | MEC: XXX MW
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Grid Code reference
| Double Point Status Indications | (each individual input identified separately for clarity) | [5 empty] | Note: Signals treated as 2-bit binary
Digital Input Signals from Sub Station to EirGrid
A1 | WINDFARM T121 WFPS 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A2 | WINDFARM T121 WFPS 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A3 | WINDFARM Feeder 1 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A4 | WINDFARM Feeder 1 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1 | Typical SLD for a wind farm connecting to the system through a 38/20 kV transformer
A5 | WINDFARM Feeder 2 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A6 | WINDFARM Feeder 2 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A7 | WINDFARM Feeder 3 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A8 | WINDFARM Feeder 3 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A9 | WINDFARM Feeder 4 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A10 | WINDFARM Feeder 4 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A11 | WINDFARM Feeder 5 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A12 | WINDFARM Feeder 5 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A13 | TSO Dispatch Control Enable Switch |  | off |  |  | WFPS | N/A | Distribution Code Signals List #1 DCC11.5.1.1 (Blocks all commands to WFPS equipment, located on WFPS side)
A14 | TSO Dispatch Control Enable Switch |  | on |  |  | WFPS | N/A | Distribution Code Signals List #1 DCC11.5.1.1 (Blocks all commands to WFPS equipment, located on WFPS side)
A15 | Dispatch Fail Market Command Lamp - WFPS Panel |  | off |  |  | WFPS | ESBN
A16 | Dispatch Fail Market Command Lamp - WFPS Panel |  | on |  |  | WFPS | ESBN
A17 | Blue Alert Lamp - WFPS Panel |  | off |  |  | WFPS | ESBN
A18 | Blue Alert Lamp - WFPS Panel |  | on |  |  | WFPS | ESBN
A19 | ESB SCADA Remote Control Switch |  | off |  |  | ESBN | ESBN
A20 | ESB SCADA Remote Control Switch |  | on |  |  | ESBN | ESBN
A21 | Reactive Device >5 Mvar 1 |  | off |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A22 | Reactive Device >5 Mvar 1 |  | on |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | WFPS | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B2 | Active Power Control facility status (feedback) |  | on |  |  | WFPS | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | WFPS | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | WFPS | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | WFPS | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | WFPS | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B7 | AVR (kV) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B8 | AVR (kV) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B9 | Q (Mvar) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B10 | Q (Mvar) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B11 | Power Factor (PF) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B12 | Power Factor (PF) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B13 | Emulated Inertia Status (Feedback) |  | off |  |  | WFPS | ESBN | Feedback from IPP to confirm status of emulated inertia service
B14 | Emulated Inertia Status (Feedback) |  | on |  |  | WFPS | ESBN | Feedback from IPP to confirm status of emulated inertia service
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Grid Code reference
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | MW | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1 (125% of Registered Capacity)
C2 | Reactive Power at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1 (150% of Reactive Power at Registered Capacity)
C3 | Voltage at LV side of Grid Connected Transformer | 0-10 | mA | 0 - 132 | kV | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1 (125% of nominal connection voltage)
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1 (125% of Registered Capacity)
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | WFPS | N/A | Grid Code Signals List #4 WFPS 1.7.1.4 (125% of Registered Capacity)
D3 | Voltage Control Setpoint (feedback) | 0-10 | mA | 99 - 132 | kV | WFPS | N/A | Grid Code Signals List #5 DCC11.5.2.3
D4 | Mvar (Q) Control Setpoint (feedback) | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
D5 | Power Factor (PF) Control Setpoint (feedback) | -10 to 0 to 10 | mA | +/- 90 | degrees | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012. Phase angle will be sent by NCC to WFPS Controller.
D6 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-12 | % | WFPS | N/A | Grid Code Modification MPID 227 Approved by CER 26/02/2013
D7 | Transformer Tap Position | 0-10 | mA | 1 to 21 | Tap | WFPS | N/A | Grid Code Signals List #5 WFPS 1.7.1.5
Analogue WTG Availability
D8 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | WFPS | N/A | Grid Code Signals List #3 WFPS 1.7.1.3
D9 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | WFPS | N/A | Grid Code Signals List #3 WFPS 1.7.1.3
D10 | Wind Farm Availability | 0-10 | mA | 0-110 | % | WFPS | N/A | Grid Code Signals List #3 WFPS 1.7.1.3
Analogue Availability
D11 | Emulated Inertia FFR availability | 0-10 | mA | 0-XX | MW | WFPS | ESBN | Provides a reading of the available MW of FFR from Emulated Inertia
D12 | Emulated Inertia POR availability | 0-10 | mA | 0-XX | MW | WFPS | ESBN | Provides a reading of the available MW of POR from Emulated Inertia
Met 1 (if Registered Capacity >= 10 MW)
D13 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
D14 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | WFPS | N/A | Grid Code Signals List #6 WFPS 1.7.1.6 (0mA = 0deg (from the North), 2.5mA = 90deg (from the East), 5mA = 180deg (from the South),7.5mA = 270deg (from West), 10mA = 360deg (from the North)).
D15 | Air Temperature 1 | 0-10 | mA | -40-70 | C | WFPS | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
D16 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
Met N (if Registered Capacity >= 10 MW)
D17 | Wind Speed N | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
D18 | Wind Direction N | 0-10 | mA | 0-360 | deg | WFPS | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
D19 | Air Temperature N | 0-10 | mA | -40-70 | C | WFPS | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
D20 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to | Distribution Code reference
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #5 WFPS 1.7.1.5
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #5 WFPS 1.7.1.5
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #5 WFPS 1.7.1.5
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #5 WFPS 1.7.1.5
E7 | Emulated Inertia Status (Feedback) |  | off | pulse | 0.5 seconds | WFPS | N/A | Control from NCC to enable emulated inertia
E8 | Emulated Inertia Status (Feedback) |  | on | pulse | 0.5 seconds | WFPS | N/A | Control from NCC to enable emulated inertia
Digital Output Signals from EirGrid to Sub Station
F1 | Blackstart Shutdown |  | off | pulse | 0.5 seconds | WFPS | N/A | Connection CB Trip/ Inhibit function
F2 | Blackstart Shutdown |  | on | pulse | 0.5 seconds | WFPS | N/A | Connection CB Trip/ Inhibit function
Strobe Enable Pulse
Digital Output Signals from EirGrid to WTG System
E9 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
E10 | Digital Output Voltage Control (kV) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E11 | Digital Output Mvar Control (Q) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E12 | Digital Output Power Factor Control (PF) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E13 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 227 Approved by CER 26/02/2013
Single Command Outputs
E14 | Voltage Control facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #5 DCC11.5.2.3
E15 | Mvar (Q) Control Facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E16 | Power Factor (PF) Control facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to | Distribution Code reference
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | WFPS | N/A | Grid Code Signals List #4 WFPS 1.7.1.4 (125% of Registered Capacity)
G2 | Analogue Voltage Control Setpoint | 4 - 20 | mA | 99 - 132 | kV | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
G3 | Analogue Mvar (Q) Control Setpoint | 4 - 20 | mA | #VALUE! | Mvar | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
G4 | Analogue Power Factor (PF) Control Setpoint | 4 - 20 | mA | +/- 90 | degrees | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
G5 | Frequency Droop Setting | 4 - 20 | mA | 0-12 | % | WFPS | N/A | Grid Code Modification MPID 227 Approved by CER 26/02/2013
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
Note on D1: Administrator: Insert the Type of the Wind Farm
Note on E1: Administrator: Insert the Registered Capacity of the WFPS
Note on A5: EirGrid Telecoms Interface Enclosure
Note on H5: No IPP involvement unless otherwise confirmed
Note on E53: +/-125%
Note on E55: 110kV: 0 to 132 kV 38kV: 0 to 45.6 kV 20kV: 0 to 24 kV
Note on E58: 0-120%
Note on E59: 0-120%
Note on E60: 110kV: 99 to 132 kV 38kV: 34.2 to 45.6 kV 20kV: 18 to 24 kV
Note on E64: Ensure tap range starts at 1: -13 to +13 should be 1 to 27 -13 to +7 should be 1 to 21
Note on E124: 0 to 125%

## 1a) Inst.Info & Contact Details
WINDFARM NAME (TLC) Information and Contact Details to be sent by WFPS via ESB Networks to EirGrid (generator_testing@EirGrid.com)
Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4
DATE
| HV SUB STATION NAME |  |  |  |  | ESBTS Team |  | Liam Boland
[6 empty] | Nessan Heaslip | Karl O'Keeffe | Noel Cowhey
| EirGrid Contact Person | Colm MacManus | PHONE: |  | (+353) 1 23 70168 | Robert Groarke | Oisín Goulding
| OSP Generic Email: Generator_testing@eirgrid.com |  |  |  |  | Frank Donnelly | Colm MacManus
| EMS Generic Email: ems.services@eirgrid.com |  |  |  |  | Liam Delany | C&T Team
[6 empty] | Niall Molloy | Ciarán Maguire
| ESBTS Project Manager | ESBTS Team | PHONE: |  | (+353) 1 7027835
| ESBTS Commissioner | ESBTS Team | PHONE: |  | (+353) 1 7027835
ESBTS Generic Email: esbts.scada.services@esb.ie
| ESB Networks (SPOC) |  | PHONE:
ESB Networks Build Generic Email: IPPdelivery@esb.ie
| ESB Networks (switchgear) |  | PHONE: |  | (+ )
| ESB Networks (metering) |  | PHONE: |  | (+ )
| WFPS Project Manager |  | PHONE: |  | (+ )
| Electrical Contractor |  | PHONE: |  | (+ )
| Turbine Contractor |  | PHONE: |  | (+ )
| Work Programme / Schedule (.mpp format) |  |  | Insert File
| Single Line Diagram |  |  | Insert file
| Site Layout Drawing on OS Map |  |  | Insert file
| Substation & Control Building Layout Drawing on OS Map |  |  | Insert file
| WFPS Energy Management System %error |  |  | %
| Directions including Map to the Wind Farm Power Station | Insert Map and brief description
| Safety & Site information | WFPS to provide details
ESBTS Standard Requirements from WFPS (may be customised for particular sites):
1) 90sq mm earth for Telecoms earth bar. 2) 35sq mm bonded from external earth grid to GPS clock antenna mounting bracket and if applicable Satellite antenna mounting bracket. 3) 48V DC Power System consisting of Switched Mode Power Supply (SMPS) with sealed cell battery. 4) If applicable - Fibre termination cabinet with fibre termination unit and fibre to distant station. 5) Satellite link consisting of Satellite transceiver and antenna if applicable. Satellite antenna preferably on a south facing wall with a clear view of the horizon. 6) Install and terminate process control and signal cables in ETI (the wiring schedule is available as a worksheet in the signal list excel file).
| ESB Telecom Services - Indicative Timelines for on site works | 1) 3 weeks notice required by ESBTS to schedule resources. 2) ~1 week to install the RTU cabinet with integrated ETI and GPS clock, GPS clock antenna. 3) ~1 week to pre commission the RTU referenced to frozen signal list with WFPS electrical and WTG contractors. 4) ~1 week to install and commission the satellite link including antenna (if applicable). 5) ~2 days to commission the fibre link (if applicable). 6) ~1 week to commission the RTU with WFPS electrical and WTG contractors.

## 1b) WFPS Wiring Completion Cert
WINDFARM NAME (TLC) |  | Type | A | XX | MW | v1.0 |  | Signals List is based on this Single Line Diagram (SLD) as inserted. | Wiring Completion Cert
EirGrid Signals, Command & Control Specification | [8 empty] | Continuity Check Complete
WFPS Wiring Completion Certificate (to EirGrid ETIE/RTU) to be sent by WFPS to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Grid Code reference
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | WINDFARM T121 WFPS 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A2 | WINDFARM T121 WFPS 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A3 | WINDFARM Feeder 1 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A4 | WINDFARM Feeder 1 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A5 | WINDFARM Feeder 2 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A6 | WINDFARM Feeder 2 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A7 | WINDFARM Feeder 3 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A8 | WINDFARM Feeder 3 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A9 | WINDFARM Feeder 4 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A10 | WINDFARM Feeder 4 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A11 | WINDFARM Feeder 5 20 kV CB |  | open |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A12 | WINDFARM Feeder 5 20 kV CB |  | closed |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A13 | TSO Dispatch Control Enable Switch |  | off |  |  | WFPS | N/A | Distribution Code Signals List #1 DCC11.5.1.1 (Blocks all commands to WFPS equipment, located on WFPS side)
A14 | TSO Dispatch Control Enable Switch |  | on |  |  | WFPS | N/A | Distribution Code Signals List #1 DCC11.5.1.1 (Blocks all commands to WFPS equipment, located on WFPS side)
A15 | Dispatch Fail Market Command Lamp - WFPS Panel |  | off |  |  | WFPS | ESBN
A16 | Dispatch Fail Market Command Lamp - WFPS Panel |  | on |  |  | WFPS | ESBN
A17 | Blue Alert Lamp - WFPS Panel |  | off |  |  | WFPS | ESBN
A18 | Blue Alert Lamp - WFPS Panel |  | on |  |  | WFPS | ESBN
A19 | ESB SCADA Remote Control Switch |  | off |  |  | ESBN | ESBN
A20 | ESB SCADA Remote Control Switch |  | on |  |  | ESBN | ESBN
A21 | Reactive Device >5 Mvar 1 |  | off |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
A22 | Reactive Device >5 Mvar 1 |  | on |  |  | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | WFPS | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B2 | Active Power Control facility status (feedback) |  | on |  |  | WFPS | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | WFPS | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | WFPS | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | WFPS | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | WFPS | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
B7 | AVR (kV) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B8 | AVR (kV) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B9 | Q (Mvar) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B10 | Q (Mvar) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B11 | Power Factor (PF) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B12 | Power Factor (PF) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
B13 | Emulated Inertia Status (Feedback) |  | off |  |  | WFPS | ESBN | Feedback from IPP to confirm status of emulated inertia service
B14 | Emulated Inertia Status (Feedback) |  | on |  |  | WFPS | ESBN | Feedback from IPP to confirm status of emulated inertia service
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to | Grid Code reference
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | MW | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1 (125% of Registered Capacity)
C2 | Reactive Power at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1 (150% of Reactive Power at Registered Capacity)
C3 | Voltage at LV side of Grid Connected Transformer | 0-10 | mA | 0 - 132 | kV | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1 (125% of nominal connection voltage)
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | WFPS | N/A | Grid Code Signals List #1 WFPS 1.7.1 (125% of Registered Capacity)
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | WFPS | N/A | Grid Code Signals List #4 WFPS 1.7.1.4 (125% of Registered Capacity)
D3 | Voltage Control Setpoint (feedback) | 0-10 | mA | 99 - 132 | kV | WFPS | N/A | Grid Code Signals List #5 DCC11.5.2.3
D4 | Mvar (Q) Control Setpoint (feedback) | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
D5 | Power Factor (PF) Control Setpoint (feedback) | -10 to 0 to 10 | mA | +/- 90 | degrees | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012. Phase angle will be sent by NCC to WFPS Controller.
D6 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-12 | % | WFPS | N/A | Grid Code Modification MPID 227 Approved by CER 26/02/2013
D7 | Transformer Tap Position | 0-10 | mA | 1 to 21 | Tap | WFPS | N/A | Grid Code Signals List #5 WFPS 1.7.1.5
Analogue WTG Availability
D8 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | WFPS | N/A | Grid Code Signals List #3 WFPS 1.7.1.3
D9 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | WFPS | N/A | Grid Code Signals List #3 WFPS 1.7.1.3
D10 | Wind Farm Availability | 0-10 | mA | 0-110 | % | WFPS | N/A | Grid Code Signals List #3 WFPS 1.7.1.3
Analogue Availability
D11 | Emulated Inertia FFR availability | 0-10 | mA | 0-XX | MW | WFPS | ESBN | Provides a reading of the available MW of FFR from Emulated Inertia
D12 | Emulated Inertia POR availability | 0-10 | mA | 0-XX | MW | WFPS | ESBN | Provides a reading of the available MW of POR from Emulated Inertia
Met 1 (if Registered Capacity >= 10 MW)
D13 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
D14 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | WFPS | N/A | Grid Code Signals List #6 WFPS 1.7.1.6 (0mA = 0deg (from the North), 2.5mA = 90deg (from the East), 5mA = 180deg (from the South),7.5mA = 270deg (from West), 10mA = 360deg (from the North)).
D15 | Air Temperature 1 | 0-10 | mA | -40-70 | C | WFPS | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
D16 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
Met N (if Registered Capacity >= 10 MW)
D17 | Wind Speed N | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
D18 | Wind Direction N | 0-10 | mA | 0-360 | deg | WFPS | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
D19 | Air Temperature N | 0-10 | mA | -40-70 | C | WFPS | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
D20 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Grid Code Signals List #6 WFPS 1.7.1.6
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to | Distribution Code reference
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #5 WFPS 1.7.1.5
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #5 WFPS 1.7.1.5
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #5 WFPS 1.7.1.5
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #5 WFPS 1.7.1.5
E7 | Emulated Inertia Status (Feedback) |  | off | pulse | 0.5 seconds | WFPS | N/A | Control from NCC to enable emulated inertia
E8 | Emulated Inertia Status (Feedback) |  | on | pulse | 0.5 seconds | WFPS | N/A | Control from NCC to enable emulated inertia
Digital Output Signals from EirGrid to Sub Station
F1 | Blackstart Shutdown |  | off | pulse | 0.5 seconds | WFPS | N/A | Connection CB Trip/ Inhibit function
F2 | Blackstart Shutdown |  | on | pulse | 0.5 seconds | WFPS | N/A | Connection CB Trip/ Inhibit function
Strobe Enable Pulse
Digital Output Signals from EirGrid to WTG System
E9 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #4 WFPS 1.7.1.4
E10 | Digital Output Voltage Control (kV) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E11 | Digital Output Mvar Control (Q) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E12 | Digital Output Power Factor Control (PF) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E13 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 227 Approved by CER 26/02/2013
Single Command Outputs
E14 | Voltage Control facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Grid Code Signals List #5 DCC11.5.2.3
E15 | Mvar (Q) Control Facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
E16 | Power Factor (PF) Control facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to | Distribution Code reference
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | WFPS | N/A | Grid Code Signals List #4 WFPS 1.7.1.4 (125% of Registered Capacity)
G2 | Analogue Voltage Control Setpoint | 4 - 20 | mA | 99 - 132 | kV | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
G3 | Analogue Mvar (Q) Control Setpoint | 4 - 20 | mA | #VALUE! | Mvar | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
G4 | Analogue Power Factor (PF) Control Setpoint | 4 - 20 | mA | +/- 90 | degrees | WFPS | N/A | Grid Code Modification MPID 212 Approved by CER 14/10/2012
G5 | Frequency Droop Setting | 4 - 20 | mA | 0-12 | % | WFPS | N/A | Grid Code Modification MPID 227 Approved by CER 26/02/2013
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
All cables for interfacing at station interface cabinet or at EirGrid telecoms interface cabinet must be clearly marked with labels for identification. |  |  |  | Confirmed  |  |  |  | How are each of the MET signals generated? E.g. From a MET mast or WTGs
All cables for interfacing at station interface cabinet or EirGrid telecoms interface cabinet must be terminated at connection terminals (i.e. stripped, crimped and marked at terminal connections). |  |  |  | Confirmed  |  |  |  | Wind Speed: Wind Direction: Air Temperature: Air Pressure:
All cables for interfacing at station interface cabinet or EirGrid telecoms interface cabinet must use colour coding agreed by all parties i.e. ESBTS & WFPS. |  |  |  | Confirmed 
All analogue and digital interface signals must be tested and simulated for compliance with the frozen signal list agreed by all parties. |  |  |  | Confirmed 
ESBTS Satellite Dish bonded with 35 sq mm earth cable onto external station earth grid. |  |  |  | Confirmed 
ESBTS GPS clock antenna bonded with 35 sq mm earth cable onto external station earth grid. |  |  |  | Confirmed 
Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4 | [6 empty] | WFPS Name / Position | 0
WFPS Signature
Date
Note on A3: Administrator: To be completed by the IPP and sent to EirGrid to schedule ESBTS site attendance to perform continuity check
Note on A5: EirGrid Telecoms Interface Enclosure

## 2) ESB Telecoms Completion Cert
WINDFARM NAME (TLC) |  | Type | A | XX | MW | v1.0 |  | Completion Cert
EirGrid Signals, Command & Control Specification | [7 empty] | Local SCADA Checks/Tests
ESB Telecoms Completion Cert to be sent by ESB Telecoms Services to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | WINDFARM T121 WFPS 20 kV CB |  | open |  |  | WFPS | N/A
A2 | WINDFARM T121 WFPS 20 kV CB |  | closed |  |  | WFPS | N/A
A3 | WINDFARM Feeder 1 20 kV CB |  | open |  |  | WFPS | N/A
A4 | WINDFARM Feeder 1 20 kV CB |  | closed |  |  | WFPS | N/A
A5 | WINDFARM Feeder 2 20 kV CB |  | open |  |  | WFPS | N/A
A6 | WINDFARM Feeder 2 20 kV CB |  | closed |  |  | WFPS | N/A
A7 | WINDFARM Feeder 3 20 kV CB |  | open |  |  | WFPS | N/A
A8 | WINDFARM Feeder 3 20 kV CB |  | closed |  |  | WFPS | N/A
A9 | WINDFARM Feeder 4 20 kV CB |  | open |  |  | WFPS | N/A
A10 | WINDFARM Feeder 4 20 kV CB |  | closed |  |  | WFPS | N/A
A11 | WINDFARM Feeder 5 20 kV CB |  | open |  |  | WFPS | N/A
A12 | WINDFARM Feeder 5 20 kV CB |  | closed |  |  | WFPS | N/A
A13 | TSO Dispatch Control Enable Switch |  | off |  |  | WFPS | N/A
A14 | TSO Dispatch Control Enable Switch |  | on |  |  | WFPS | N/A
A15 | Dispatch Fail Market Command Lamp - WFPS Panel |  | off |  |  | WFPS | ESBN
A16 | Dispatch Fail Market Command Lamp - WFPS Panel |  | on |  |  | WFPS | ESBN
A17 | Blue Alert Lamp - WFPS Panel |  | off |  |  | WFPS | ESBN
A18 | Blue Alert Lamp - WFPS Panel |  | on |  |  | WFPS | ESBN
A19 | ESB SCADA Remote Control Switch |  | off |  |  | ESBN | ESBN
A20 | ESB SCADA Remote Control Switch |  | on |  |  | ESBN | ESBN
A21 | Reactive Device >5 Mvar 1 |  | off |  |  | WFPS | N/A
A22 | Reactive Device >5 Mvar 1 |  | on |  |  | WFPS | N/A
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | WFPS | N/A
B2 | Active Power Control facility status (feedback) |  | on |  |  | WFPS | N/A
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | WFPS | N/A
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | WFPS | N/A
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | WFPS | N/A
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | WFPS | N/A
B7 | AVR (kV) Control facility status (feedback) |  | off |  |  | WFPS | N/A
B8 | AVR (kV) Control facility status (feedback) |  | on |  |  | WFPS | N/A
B9 | Q (Mvar) Control facility status (feedback) |  | off |  |  | WFPS | N/A
B10 | Q (Mvar) Control facility status (feedback) |  | on |  |  | WFPS | N/A
B11 | Power Factor (PF) Control facility status (feedback) |  | off |  |  | WFPS | N/A
B12 | Power Factor (PF) Control facility status (feedback) |  | on |  |  | WFPS | N/A
B13 | Emulated Inertia Status (Feedback) |  | off |  |  | WFPS | ESBN
B14 | Emulated Inertia Status (Feedback) |  | on |  |  | WFPS | ESBN
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | MW | WFPS | N/A
C2 | Reactive Power at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | N/A
C3 | Voltage at LV side of Grid Connected Transformer | 0-10 | mA | 0 - 132 | kV | WFPS | N/A
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | WFPS | N/A
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | WFPS | N/A
D3 | Voltage Control Setpoint (feedback) | 0-10 | mA | 99 - 132 | kV | WFPS | N/A
D4 | Mvar (Q) Control Setpoint (feedback) | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | N/A
D5 | Power Factor (PF) Control Setpoint (feedback) | -10 to 0 to 10 | mA | +/- 90 | degrees | WFPS | N/A
D6 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-12 | % | WFPS | N/A
D7 | Transformer Tap Position | 0-10 | mA | 1 to 21 | Tap | WFPS | N/A
Analogue WTG Availability
D8 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | WFPS | N/A
D9 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | WFPS | N/A
D10 | Wind Farm Availability | 0-10 | mA | 0-110 | % | WFPS | N/A
Analogue Availability
D11 | Emulated Inertia FFR availability | 0-10 | mA | 0-XX | MW | WFPS | ESBN
D12 | Emulated Inertia POR availability | 0-10 | mA | 0-XX | MW | WFPS | ESBN
Met 1 (if Registered Capacity >= 10 MW)
D13 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | WFPS | N/A
D14 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | WFPS | N/A
D15 | Air Temperature 1 | 0-10 | mA | -40-70 | C | WFPS | N/A
D16 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | WFPS | N/A
Met N (if Registered Capacity >= 10 MW)
D17 | Wind Speed N | 0-10 | mA | 0-70 | m/s | WFPS | N/A
D18 | Wind Direction N | 0-10 | mA | 0-360 | deg | WFPS | N/A
D19 | Air Temperature N | 0-10 | mA | -40-70 | C | WFPS | N/A
D20 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | WFPS | N/A
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | WFPS | N/A
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | WFPS | N/A
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | WFPS | N/A
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | WFPS | N/A
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | WFPS | N/A
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | WFPS | N/A
E7 | Emulated Inertia Status (Feedback) |  | off | pulse | 0.5 seconds | WFPS | N/A
E8 | Emulated Inertia Status (Feedback) |  | on | pulse | 0.5 seconds | WFPS | N/A
Digital Output Signals from EirGrid to Sub Station
F1 | Blackstart Shutdown |  | off | pulse | 0.5 seconds | WFPS | N/A
F2 | Blackstart Shutdown |  | on | pulse | 0.5 seconds | WFPS | N/A
Strobe Enable Pulse
Digital Output Signals from EirGrid to WTG System
E9 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A
E10 | Digital Output Voltage Control (kV) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A
E11 | Digital Output Mvar Control (Q) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A
E12 | Digital Output Power Factor Control (PF) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A
E13 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | WFPS | N/A
Single Command Outputs
E14 | Voltage Control facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A
E15 | Mvar (Q) Control Facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A
E16 | Power Factor (PF) Control facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | WFPS | N/A
G2 | Analogue Voltage Control Setpoint | 4 - 20 | mA | 99 - 132 | kV | WFPS | N/A
G3 | Analogue Mvar (Q) Control Setpoint | 4 - 20 | mA | #VALUE! | Mvar | WFPS | N/A
G4 | Analogue Power Factor (PF) Control Setpoint | 4 - 20 | mA | +/- 90 | degrees | WFPS | N/A
G5 | Frequency Droop Setting | 4 - 20 | mA | 0-12 | % | WFPS | N/A
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
All cables for interfacing at station interface cabinet or at EirGrid telecoms interface cabinet are installed and correct. |  |  |  | Confirmed  |  |  | ESBTS Name / Position | ESBTS Team
ESBTS Signature
Date
| NOTE: Non operable WFPS signals will result in rescheduling for re-commissioning and require another Joint Signals Test Cert to be performed. |  | Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4
Note on A5: EirGrid Telecoms Interface Enclosure

## 2 a) EMS Database Setup Cert
WINDFARM NAME (TLC) |  | Type | A | XX | MW | v1.0
EirGrid Signals, Command & Control Specification
Energy Management System (EMS) Database setup Certificate
Completion Cert
Continuity Check Complete
Generator Modelled
Lines Modelled
Station Modelled
Calculations Updated
RTU Modelled
Display Work Completed:
WF SLD
Station SLD
Station List
Windfarm List
Embedded Wind
Windfarm Control
Station Wind MW
Wind Overview
Windfarm Availability Data
Blue Alert Page
Windfarm Weather Data
DCC signals provided via ICCP
EMS Name
EMS Signature
Date
EirGrid Internal Document - no IPP requirements. For Information only
Note on A3: Administrator: DCC to be Informed

## 3)Pre Energ. Sign&Con Test Cert
WINDFARM NAME (TLC) |  | Type | A | XX | MW | v1.0 |  | Pre Energisation Signals and Controls Test
EirGrid Signals, Command & Control Specification | [7 empty] | Simulated □/Real □ value tested | mA Range | Value Range | Comment
Pre Energisation Signals & Controls Certificate to be sent by ESBT to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | WINDFARM T121 WFPS 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A2 | WINDFARM T121 WFPS 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A3 | WINDFARM Feeder 1 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A4 | WINDFARM Feeder 1 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A5 | WINDFARM Feeder 2 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A6 | WINDFARM Feeder 2 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A7 | WINDFARM Feeder 3 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A8 | WINDFARM Feeder 3 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A9 | WINDFARM Feeder 4 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A10 | WINDFARM Feeder 4 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A11 | WINDFARM Feeder 5 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A12 | WINDFARM Feeder 5 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A13 | TSO Dispatch Control Enable Switch |  | off |  |  | WFPS | N/A | Real □
A14 | TSO Dispatch Control Enable Switch |  | on |  |  | WFPS | N/A | Real □
A15 | Dispatch Fail Market Command Lamp - WFPS Panel |  | off |  |  | WFPS | ESBN | Real □
A16 | Dispatch Fail Market Command Lamp - WFPS Panel |  | on |  |  | WFPS | ESBN | Real □
A17 | Blue Alert Lamp - WFPS Panel |  | off |  |  | WFPS | ESBN | Real □
A18 | Blue Alert Lamp - WFPS Panel |  | on |  |  | WFPS | ESBN | Real □
A19 | ESB SCADA Remote Control Switch |  | off |  |  | ESBN | ESBN | Real □
A20 | ESB SCADA Remote Control Switch |  | on |  |  | ESBN | ESBN | Real □
A21 | Reactive Device >5 Mvar 1 |  | off |  |  | WFPS | N/A | Real □
A22 | Reactive Device >5 Mvar 1 |  | on |  |  | WFPS | N/A | Real □
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | WFPS | N/A | Simulated □
B2 | Active Power Control facility status (feedback) |  | on |  |  | WFPS | N/A | Simulated □
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | WFPS | N/A | Simulated □
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | WFPS | N/A | Simulated □
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | WFPS | N/A | Simulated □
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | WFPS | N/A | Simulated □
B7 | AVR (kV) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Simulated □
B8 | AVR (kV) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Simulated □
B9 | Q (Mvar) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Simulated □
B10 | Q (Mvar) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Simulated □
B11 | Power Factor (PF) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Simulated □
B12 | Power Factor (PF) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Simulated □
B13 | Emulated Inertia Status (Feedback) |  | off |  |  | WFPS | ESBN | Simulated □
B14 | Emulated Inertia Status (Feedback) |  | on |  |  | WFPS | ESBN | Simulated □
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | MW | WFPS | N/A | Real □
C2 | Reactive Power at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | N/A | Real □
C3 | Voltage at LV side of Grid Connected Transformer | 0-10 | mA | 0 - 132 | kV | WFPS | N/A | Real □
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | WFPS | N/A | Simulated □
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | WFPS | N/A | Simulated □
D3 | Voltage Control Setpoint (feedback) | 0-10 | mA | 99 - 132 | kV | WFPS | N/A | Simulated □
D4 | Mvar (Q) Control Setpoint (feedback) | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | N/A | Simulated □
D5 | Power Factor (PF) Control Setpoint (feedback) | -10 to 0 to 10 | mA | +/- 90 | degrees | WFPS | N/A | Simulated □
D6 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-12 | % | WFPS | N/A | Simulated □
D7 | Transformer Tap Position | 0-10 | mA | 1 to 21 | Tap | WFPS | N/A | Simulated □
Analogue WTG Availability
D8 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | WFPS | N/A | Simulated □
D9 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | WFPS | N/A | Simulated □
D10 | Wind Farm Availability | 0-10 | mA | 0-110 | % | WFPS | N/A | Simulated □
Analogue Availability
D11 | Emulated Inertia FFR availability | 0-10 | mA | 0-XX | MW | WFPS | ESBN | Simulated □
D12 | Emulated Inertia POR availability | 0-10 | mA | 0-XX | MW | WFPS | ESBN | Simulated □
Met 1 (if Registered Capacity >= 10 MW)
D13 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Simulated □
D14 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | WFPS | N/A | Simulated □
D15 | Air Temperature 1 | 0-10 | mA | -40-70 | C | WFPS | N/A | Simulated □
D16 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Simulated □
Met N (if Registered Capacity >= 10 MW)
D17 | Wind Speed N | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Simulated □
D18 | Wind Direction N | 0-10 | mA | 0-360 | deg | WFPS | N/A | Simulated □
D19 | Air Temperature N | 0-10 | mA | -40-70 | C | WFPS | N/A | Simulated □
D20 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Simulated □
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E7 | Emulated Inertia Status (Feedback) |  | off | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E8 | Emulated Inertia Status (Feedback) |  | on | pulse | 0.5 seconds | WFPS | N/A | Simulated □
Digital Output Signals from EirGrid to Sub Station
F1 | Blackstart Shutdown |  | off | pulse | 0.5 seconds | WFPS | N/A | Simulated □
F2 | Blackstart Shutdown |  | on | pulse | 0.5 seconds | WFPS | N/A | Simulated □
Strobe Enable Pulse
Digital Output Signals from EirGrid to WTG System
E9 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E10 | Digital Output Voltage Control (kV) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E11 | Digital Output Mvar Control (Q) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E12 | Digital Output Power Factor Control (PF) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E13 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Simulated □
Single Command Outputs
E14 | Voltage Control facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E15 | Mvar (Q) Control Facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Simulated □
E16 | Power Factor (PF) Control facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Simulated □
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | WFPS | N/A | Simulated □
G2 | Analogue Voltage Control Setpoint | 4 - 20 | mA | 99 - 132 | kV | WFPS | N/A | Simulated □
G3 | Analogue Mvar (Q) Control Setpoint | 4 - 20 | mA | #VALUE! | Mvar | WFPS | N/A | Simulated □
G4 | Analogue Power Factor (PF) Control Setpoint | 4 - 20 | mA | +/- 90 | degrees | WFPS | N/A | Simulated □
G5 | Frequency Droop Setting | 4 - 20 | mA | 0-12 | % | WFPS | N/A | Simulated □
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
Simulation Point
Simulation Method
[6 empty] | WFPS Name / Position |  | 0
WFPS Signature
EMS Name
EMS Signature
| NOTE: Non operable WFPS signals will result in rescheduling for re-commissioning and require another Joint Signals Test Cert to be performed. |  |  |  |  | ESB Telecoms Name / Position |  | ESBTS Team
| Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4 |  |  |  |  | ESB Telecoms Signature
Date
Note on I1: Administrator: ESBTS Commission from NCC control desk to / via ETI to IPP plant.
Note on I2: Administrator: the electrical characteristics of IPP signals not tested due to plant unavailability must be simulated by IPP.
Note on A5: EirGrid Telecoms Interface Enclosure

## 4) Post Ener Pre Grid Code Cert
WINDFARM NAME (TLC) |  | Type | A | XX | MW | v1.0 |  | Post Energisation Signals and Controls Test
EirGrid Signals, Command & Control Specification | [7 empty] | Simulated □/Real □ value tested | mA Range | Value Range | Comment
Post Energisation Signals and Controls (Pre Grid Code Check) Cert to be sent by ESBT to EirGrid (generator_testing@eirgrid.com)
ETIE Ref | Digital Input Signals (signals sent to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
| Double Point Status Indications | (each individual input identified separately for clarity)
Digital Input Signals from Sub Station to EirGrid
A1 | WINDFARM T121 WFPS 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A2 | WINDFARM T121 WFPS 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A3 | WINDFARM Feeder 1 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A4 | WINDFARM Feeder 1 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A5 | WINDFARM Feeder 2 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A6 | WINDFARM Feeder 2 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A7 | WINDFARM Feeder 3 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A8 | WINDFARM Feeder 3 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A9 | WINDFARM Feeder 4 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A10 | WINDFARM Feeder 4 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A11 | WINDFARM Feeder 5 20 kV CB |  | open |  |  | WFPS | N/A | Real □
A12 | WINDFARM Feeder 5 20 kV CB |  | closed |  |  | WFPS | N/A | Real □
A13 | TSO Dispatch Control Enable Switch |  | off |  |  | WFPS | N/A | Real □
A14 | TSO Dispatch Control Enable Switch |  | on |  |  | WFPS | N/A | Real □
A15 | Dispatch Fail Market Command Lamp - WFPS Panel |  | off |  |  | WFPS | ESBN | Real □
A16 | Dispatch Fail Market Command Lamp - WFPS Panel |  | on |  |  | WFPS | ESBN | Real □
A17 | Blue Alert Lamp - WFPS Panel |  | off |  |  | WFPS | ESBN | Real □
A18 | Blue Alert Lamp - WFPS Panel |  | on |  |  | WFPS | ESBN | Real □
A19 | ESB SCADA Remote Control Switch |  | off |  |  | ESBN | ESBN | Real □
A20 | ESB SCADA Remote Control Switch |  | on |  |  | ESBN | ESBN | Real □
A21 | Reactive Device >5 Mvar 1 |  | off |  |  | WFPS | N/A | Real □
A22 | Reactive Device >5 Mvar 1 |  | on |  |  | WFPS | N/A | Real □
Digital Input Signals from WTG System to EirGrid
B1 | Active Power Control facility status (feedback) |  | off |  |  | WFPS | N/A | Real □
B2 | Active Power Control facility status (feedback) |  | on |  |  | WFPS | N/A | Real □
B3 | Frequency Response System Mode Status (feedback) |  | off |  |  | WFPS | N/A | Real □
B4 | Frequency Response System Mode Status (feedback) |  | on |  |  | WFPS | N/A | Real □
B5 | Frequency Response Curve (feedback) |  | Curve 1 |  |  | WFPS | N/A | Real □
B6 | Frequency Response Curve (feedback) |  | Curve 2 |  |  | WFPS | N/A | Real □
B7 | AVR (kV) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Real □
B8 | AVR (kV) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Real □
B9 | Q (Mvar) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Real □
B10 | Q (Mvar) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Real □
B11 | Power Factor (PF) Control facility status (feedback) |  | off |  |  | WFPS | N/A | Real □
B12 | Power Factor (PF) Control facility status (feedback) |  | on |  |  | WFPS | N/A | Real □
B13 | Emulated Inertia Status (Feedback) |  | off |  |  | WFPS | ESBN | Real □
B14 | Emulated Inertia Status (Feedback) |  | on |  |  | WFPS | ESBN | Real □
Recommended cable 15-pair, 15 x 2 x 0.6sqmm, Twisted-Pair (TP), stranded
ETIE Ref | Analogue Input Signals (to EirGrid) |  |  |  |  | Provided by | TSO Pass-through to
Analogue Input Signals from Sub Station to EirGrid
C1 | Active Power Output at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | MW | WFPS | N/A | Real □
C2 | Reactive Power at LV side of Grid Connected Transformer | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | N/A | Real □
C3 | Voltage at LV side of Grid Connected Transformer | 0-10 | mA | 0 - 132 | kV | WFPS | N/A | Real □
Analogue Input Signals from WTG System to EirGrid
D1 | Available Active Power | 0-10 | mA | #VALUE! | MW | WFPS | N/A | Real □
D2 | Active Power Control Setpoint (feedback) | 0-10 | mA | #VALUE! | MW | WFPS | N/A | Real □
D3 | Voltage Control Setpoint (feedback) | 0-10 | mA | 99 - 132 | kV | WFPS | N/A | Real □
D4 | Mvar (Q) Control Setpoint (feedback) | -10 to 0 to 10 | mA | #VALUE! | Mvar | WFPS | N/A | Real □
D5 | Power Factor (PF) Control Setpoint (feedback) | -10 to 0 to 10 | mA | +/- 90 | degrees | WFPS | N/A | Real □
D6 | Frequency Droop Setting (feedback) | 0-10 | mA | 0-12 | % | WFPS | N/A | Real □
D7 | Transformer Tap Position | 0-10 | mA | 1 to 21 | Tap | WFPS | N/A | Real □
Analogue WTG Availability
D8 | %WTG not generating due to high wind | 0-10 | mA | 0-110 | % | WFPS | N/A | Real □
D9 | %WTG not generating due to low wind | 0-10 | mA | 0-110 | % | WFPS | N/A | Real □
D10 | Wind Farm Availability | 0-10 | mA | 0-110 | % | WFPS | N/A | Real □
Analogue Availability
D11 | Emulated Inertia FFR availability | 0-10 | mA | 0-XX | MW | WFPS | ESBN | Real □
D12 | Emulated Inertia POR availability | 0-10 | mA | 0-XX | MW | WFPS | ESBN | Real □
Met 1 (if Registered Capacity >= 10 MW)
D13 | Wind Speed 1 | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Real □
D14 | Wind Direction 1 | 0-10 | mA | 0-360 | deg | WFPS | N/A | Real □
D15 | Air Temperature 1 | 0-10 | mA | -40-70 | C | WFPS | N/A | Real □
D16 | Air Pressure 1 | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Real □
Met N (if Registered Capacity >= 10 MW)
D17 | Wind Speed N | 0-10 | mA | 0-70 | m/s | WFPS | N/A | Real □
D18 | Wind Direction N | 0-10 | mA | 0-360 | deg | WFPS | N/A | Real □
D19 | Air Temperature N | 0-10 | mA | -40-70 | C | WFPS | N/A | Real □
D20 | Air Pressure N | 0-10 | mA | 735-1060 | mBar | WFPS | N/A | Real □
Recommended cable 25-pair cable: 25 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
ETIE Ref | Digital Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
| Double Command Outputs | (each individual relay output identified separately)
Digital Output Signals from EirGrid to WTG System
E1 | Active Power Control facility status |  | off | pulse | 0.5 seconds | WFPS | N/A | Real □
E2 | Active Power Control facility status |  | on | pulse | 0.5 seconds | WFPS | N/A | Real □
E3 | Frequency Response System Mode Status |  | off | pulse | 0.5 seconds | WFPS | N/A | Real □
E4 | Frequency Response System Mode Status |  | on | pulse | 0.5 seconds | WFPS | N/A | Real □
E5 | Frequency Response Curve Select |  | Curve 1 | pulse | 0.5 seconds | WFPS | N/A | Real □
E6 | Frequency Response Curve Select |  | Curve 2 | pulse | 0.5 seconds | WFPS | N/A | Real □
E7 | Emulated Inertia Status (Feedback) |  | off | pulse | 0.5 seconds | WFPS | N/A | Real □
E8 | Emulated Inertia Status (Feedback) |  | on | pulse | 0.5 seconds | WFPS | N/A | Real □
Digital Output Signals from EirGrid to Sub Station
F1 | Blackstart Shutdown |  | off | pulse | 0.5 seconds | WFPS | N/A | Real □
F2 | Blackstart Shutdown |  | on | pulse | 0.5 seconds | WFPS | N/A | Real □
Strobe Enable Pulse
Digital Output Signals from EirGrid to WTG System
E9 | Digital Output Active Power Control Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Real □
E10 | Digital Output Voltage Control (kV) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Real □
E11 | Digital Output Mvar Control (Q) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Real □
E12 | Digital Output Power Factor Control (PF) Setpoint Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Real □
E13 | Digital Output Frequency Droop Setting Enable |  |  | pulse | 0.5 seconds | WFPS | N/A | Real □
Single Command Outputs
E14 | Voltage Control facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Real □
E15 | Mvar (Q) Control Facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Real □
E16 | Power Factor (PF) Control facility status ON |  | on | pulse | 0.5 seconds | WFPS | N/A | Real □
Recommended Cable 15-pair Screened Cable : 15 x 2 x 0.6sqmm, Twisted-Pair ( TP).
ETIE Ref | Analogue Output Signals (from EirGrid) |  |  |  |  | Provided to | TSO Pass-through to
Analogue Output Signals from EirGrid to WTG System
G1 | Analogue Output Active Power Control Setpoint | 4 - 20 | mA | #VALUE! | MW | WFPS | N/A | Real □
G2 | Analogue Voltage Control Setpoint | 4 - 20 | mA | 99 - 132 | kV | WFPS | N/A | Real □
G3 | Analogue Mvar (Q) Control Setpoint | 4 - 20 | mA | #VALUE! | Mvar | WFPS | N/A | Real □
G4 | Analogue Power Factor (PF) Control Setpoint | 4 - 20 | mA | +/- 90 | degrees | WFPS | N/A | Real □
G5 | Frequency Droop Setting | 4 - 20 | mA | 0-12 | % | WFPS | N/A | Real □
Recommended cable 5-pair cable: 5 x 2 x 0.6sqmm TP, stranded, individually screened pairs. Screens to be terminated by WFPS.
Confirm the source of the MET signals e.g. from MET mast or from WTGs
| Wind Speed source: |  |  |  |  | WFPS Name |  | 0
| Wind Direction source: |  |  |  |  | WFPS Signature
| Air Temperature source: |  |  |  |  | EMS Name
| Air Pressure source: |  |  |  |  | EMS Signature
| NOTE: Non operable WFPS signals will result in rescheduling for re-commissioning and require another Joint Signals Test Cert to be performed. |  |  |  |  | ESB Telecoms Name / Position |  | ESBTS Team
| Note: That for the duration of the Post Energization Test, there should be NO external influencing factors |  |  |  |  | ESB Telecoms Signature
| Information may be sent to by email: generator_testing@eirgrid.com, Fax: +353 (0)1 661 5375 or Post to: Operational Services & Performance, EirGrid, The Oval, 160 Shelbourne Road, Ballsbridge, Dublin 4 |  |  |  |  | Date
Note on A5: EirGrid Telecoms Interface Enclosure

## ETIE
EirGrid Telecoms Interface Enclosure (ETIE)
Typical EirGrid RTU cabinet with integrated ETI and GPS clock 2.0m x 0.8m x 0.6m (rear access not required).
Note: This is for a typical installation and may vary from project to project. Any queries should be directed to generator_testing@eirgrid.com or esbts.scada.services@esb.ie
ETIE General Description
There will be four rows of terminals labelled Row 1, 2, 3, 4 as shown in the Layout drawing and Photograph above
Trunking shall be separated into WFPS and EirGrid Telecoms trunking.
EirGrid Telecoms cabling to be in EirGrid Telecoms designated trunking only
WFPS cabling to be in WFPS designated trunking only
Access to terminals will be as follows:
Upper side to be used for EirGrid Telecoms use only
Lower side to be used for WFPS use only
Isolating link to sever all connection between the WFPS connection and EirGrid Telecoms connection
Command terminals to be covered with a Perspex cover and labelled "DO NOT ENERGISE"
Earthing of cabinet to be completed in accordance with 35 sq mm earth cable to EirGrid Telecoms earth bar

## ETIE Layout
Designation: Indications/Signals |  | ETIE Ref | ETIE ROW 1
POSITIVE 24V or 48V DC DOUBLE POINT INDICATION |  |  | +
WINDFARM T121 WFPS 20 kV CB | open | A1 | 1
WINDFARM T121 WFPS 20 kV CB | closed | A2 | 2
WINDFARM Feeder 1 20 kV CB | open | A3 | 3
WINDFARM Feeder 1 20 kV CB | closed | A4 | 4
WINDFARM Feeder 2 20 kV CB | open | A5 | 5
WINDFARM Feeder 2 20 kV CB | closed | A6 | 6
WINDFARM Feeder 3 20 kV CB | open | A7 | 7
WINDFARM Feeder 3 20 kV CB | closed | A8 | 8
WINDFARM Feeder 4 20 kV CB | open | A9 | 9
WINDFARM Feeder 4 20 kV CB | closed | A10 | 10
WINDFARM Feeder 5 20 kV CB | open | A11 | 11
WINDFARM Feeder 5 20 kV CB | closed | A12 | 12
TSO Dispatch Control Enable Switch | off | A13 | 13
TSO Dispatch Control Enable Switch | on | A14 | 14
Dispatch Fail Market Command Lamp - WFPS Panel | off | A15 | 15
Dispatch Fail Market Command Lamp - WFPS Panel | on | A16 | 16
Reactive Device >5 Mvar 1 | off | A21 | 17
Reactive Device >5 Mvar 1 | on | A22 | 18
Active Power Control facility status (feedback) | off | B1 | 19
Active Power Control facility status (feedback) | on | B2 | 20
Frequency Response System Mode Status (feedback) | off | B3 | 21
Frequency Response System Mode Status (feedback) | on | B4 | 22
Frequency Response Curve (feedback) | Curve 1 | B5 | 23
Frequency Response Curve (feedback) | Curve 2 | B6 | 24
AVR (kV) Control facility status (feedback) | off | B7 | 25
AVR (kV) Control facility status (feedback) | on | B8 | 26
Q (Mvar) Control facility status (feedback) | off | B9 | 27
Q (Mvar) Control facility status (feedback) | on | B10 | 28
Power Factor (PF) Control facility status (feedback) | off | B11 | 29
Power Factor (PF) Control facility status (feedback) | on | B12 | 30
Emulated Inertia Status (Feedback) | off | B13 | 31
Emulated Inertia Status (Feedback) | on | B14 | 32
33
34
35
36
37
38
POSITIVE 24V or 48V DC SINGLE POINT INDICATION |  |  | +
41
42
43
44
45
46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
Designation: Measurands | Polarity | ETIE Ref | ETIE ROW 2
Active Power Output at LV side of Grid Connected Transformer | + | C1 | 1
Active Power Output at LV side of Grid Connected Transformer | - | C1 | 2
Reactive Power at LV side of Grid Connected Transformer | + | C2 | 3
Reactive Power at LV side of Grid Connected Transformer | - | C2 | 4
Voltage at LV side of Grid Connected Transformer | + | C3 | 5
Voltage at LV side of Grid Connected Transformer | - | C3 | 6
Available Active Power | + | D1 | 7
Available Active Power | - | D1 | 8
Active Power Control Setpoint (feedback) | + | D2 | 9
Active Power Control Setpoint (feedback) | - | D2 | 10
Voltage Control Setpoint (feedback) | + | D3 | 11
Voltage Control Setpoint (feedback) | - | D3 | 12
Mvar (Q) Control Setpoint (feedback) | + | D4 | 13
Mvar (Q) Control Setpoint (feedback) | - | D4 | 14
Power Factor (PF) Control Setpoint (feedback) | + | D5 | 15
Power Factor (PF) Control Setpoint (feedback) | - | D5 | 16
Frequency Droop Setting (feedback) | + | D6 | 17
Frequency Droop Setting (feedback) | - | D6 | 18
Transformer Tap Position | + | D7 | 19
Transformer Tap Position | - | D7 | 20
%WTG not generating due to high wind | + | D8 | 21
%WTG not generating due to high wind | - | D8 | 22
%WTG not generating due to low wind | + | D9 | 23
%WTG not generating due to low wind | - | D9 | 24
Wind Farm Availability | + | D10 | 25
Wind Farm Availability | - | D10 | 26
Emulated Inertia FFR availability | + | D11 | 27
Emulated Inertia FFR availability | - | D11 | 28
Emulated Inertia POR availability | + | D12 | 29
Emulated Inertia POR availability | - | D12 | 30
Wind Speed 1 | + | D13 | 31
Wind Speed 1 | - | D13 | 32
Wind Direction 1 | + | D14 | 33
Wind Direction 1 | - | D14 | 34
Air Temperature 1 | + | D15 | 35
Air Temperature 1 | - | D15 | 36
Air Pressure 1 | + | D16 | 37
Air Pressure 1 | - | D16 | 38
Wind Speed N | + | D17 | 39
Wind Speed N | - | D17 | 40
Wind Direction N | + | D18 | 41
Wind Direction N | - | D18 | 42
Air Temperature N | + | D19 | 43
Air Temperature N | - | D19 | 44
Air Pressure N | + | D20 | 45
Air Pressure N | - | D20 | 46
47
48
49
50
51
52
53
54
55
56
57
58
59
60
61
62
63
64
Designation: Commands | Polarity | ETIE Ref | ETIE ROW 3
Analogue Output Active Power Control Setpoint | + | G1 | 1
Analogue Output Active Power Control Setpoint | - | G1 | 2
Analogue Voltage Control Setpoint | + | G2 | 3
Analogue Voltage Control Setpoint | - | G2 | 4
Analogue Mvar (Q) Control Setpoint | + | G3 | 5
Analogue Mvar (Q) Control Setpoint | - | G3 | 6
Analogue Power Factor (PF) Control Setpoint | + | G4 | 7
Analogue Power Factor (PF) Control Setpoint | - | G4 | 8
Frequency Droop Setting | + | G5 | 9
Frequency Droop Setting | - | G5 | 10
TBC
TBC
Designation: Controls |  | ETIE Ref | ETIE ROW 4
Active Power Control facility status | off | E1 | 1
Command Negative |  |  | 2
Active Power Control facility status | on | E2 | 3
Frequency Response System Mode Status | off | E3 | 4
Command Negative |  |  | 5
Frequency Response System Mode Status | on | E4 | 6
Frequency Response Curve Select | Curve 1 | E5 | 7
Command Negative |  |  | 8
Frequency Response Curve Select | Curve 2 | E6 | 9
Emulated Inertia Status (Feedback) | off | E7 | 10
Command Negative |  |  | 11
Emulated Inertia Status (Feedback) | on | E8 | 12
Blackstart Shutdown | off | F1 | 13
Command Negative |  |  | 14
Blackstart Shutdown | on | F2 | 15
Command Output |  |  | 16
Command Negative |  |  | 17
Command Output |  |  | 18
Command Output |  |  | 19
Command Negative |  |  | 20
Command Output |  |  | 21
Command Output |  |  | 22
Command Negative |  |  | 23
Command Output |  |  | 24
Command Output |  |  | 25
Command Negative |  |  | 26
Command Output |  |  | 27
Command Output |  |  | 28
Command Negative |  |  | 29
Command Output |  |  | 30
Single Controls |  |  | +
31
32
33
34
35
36
Single Command Outputs |  | E14 | 37
|  | E14 | 38
Voltage Control facility status ON |  | E15 | 39
|  | E15 | 40
Mvar (Q) Control Facility status ON |  | E16 | 41
|  | E16 | 42
Digital Output Frequency Droop Setting Enable |  | E13 | 43
|  | E13 | 44
Digital Output Active Power Control Setpoint Enable |  | E9 | 45
|  | E9 | 46
Digital Output Voltage Control (kV) Setpoint Enable |  | E10 | 47
|  | E10 | 48
Digital Output Mvar Control (Q) Setpoint Enable |  | E11 | 49
|  | E11 | 50
Digital Output Power Factor Control (PF) Setpoint Enable |  | E12 | 51
|  | E12 | 52
Note on D2: There should be no Gaps between the individual Wiring references for Row 1, 2 and 4
Note on D66: Administrator: Administrator: There should be no Gaps between the individual Wiring references for Row 1, 2 and 4
Note on D131: Administrator: There is a gap between the off / on commands for command negative
Note on D144: Administrator: There should be no Gaps between the individual Wiring references for Row 1, 2 and 4

## Freq,Ramping,Voltage Settings
Frequency, Ramp Rate and Voltage Settings to be implemented in Wind Farm Control System
Definitions:
| AAP | Available Active Power
| DMOL | Designed Minimum Operating Level
| APC | Active Power Control
Frequency Response Mode On | [5 empty] | Frequency Response Diagrams
Curve 1: Wind Following Mode
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f < 48 |  | 100% of AAP
|  | FA | 48 | PA | 100% of AAP
|  | Under Frequency Response | 48 < f < 49.8 |  | 100% of AAP
|  | FB | f = 49.8 | PB | 100% of AAP
|  | +/-0.2Hz Deadband | 49.8 < f < 50.2 |  | 100% of AAP
|  | FC | f = 50.2 | PC | 100% of AAP
|  | Over Frequency Response | 50.2 < f < 51.9 |  | AAP + ∆MW2
|  | FD | f = 51.9 | PD | Minimum of: AAP and DMOL
|  | FE | f = 52 | PE | 0%3
|  |  | f > 52 |  | 0%3
Curve 1: Active Power Control Mode
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f < 48 |  | 100% of AAP
|  | FA | f = 48 | PA | 100% of AAP
|  | Under Frequency Response | 48 < f < 49.985 |  | Minimum of: APC Setpoint + ∆MW and AAP
|  | FB | f = 49.985 | PB | Minimum of: APC Setpoint and AAP
|  | +/-0.015Hz Deadband | 49.985 < f < 50.015 |  | Minimum of: APC Setpoint and AAP
|  | FC | f = 50.015 | PC | Minimum of: APC Setpoint and AAP
|  | Over Frequency Response | 50.015 < f < 51.9 |  | Minimum of: APC Setpoint + ∆MW and AAP + ∆MW1, 2
|  | FD | f = 51.9 | PD | Minimum of: APC Setpoint and AAP and DMOL
|  | FE | f = 52 | PE | 0%3
|  |  | f > 52 |  | 0%3
Curve 2: Wind Following Mode
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f <49.3 |  | 100% of AAP
|  | FA | f = 49.3 | PA | 100% of AAP
|  | Under Frequency Response | 49.3 < f < 49.985 |  | 95% of Available Active Power + ∆MW
|  | FB | f = 49.985 | PB | 95% of Available Active Power. This is = to 5% Reserve.
|  | +/-0.015Hz Deadband | 49.985 < f < 50.015 |  | 95% of Available Active Power. This is = to 5% Reserve.
|  | FC | f = 50.015 | PC | 95% of Available Active Power. This is = to 5% Reserve.
|  | Over Frequency Response | 50.015 < f < 51.9 |  | 95% of AAP + ∆MW2
|  | FD | f = 51.9 | PD | Minimum of: AAP and DMOL
|  | FE | f = 52 | PE | 0%3
|  |  | f > 52 |  | 0%3
Curve 2: Active Power Control Mode
|  |  | Transmission System Frequency f (Hz) |  | Required Active Power Output
|  |  | f < 49.3 |  | 100% of AAP
|  | FA | f = 49.3 | PA | 100% of AAP
|  | Under Frequency Response | 49.3 < f < 49.985 |  | Minimum of: APC Setpoint + ∆MW and 95% of AAP + ∆MW
|  | FB | f = 49.985 | PB | Minimum of: APC Setpoint and 95% of AAP
|  | +/-0.015Hz Deadband | 49.985 < f < 50.015 |  | Minimum of: APC Setpoint and 95% of AAP
|  | FC | f = 50.015 | PC | Minimum of: APC Setpoint and 95% of AAP
|  | Over Frequency Response | 50.015 < f < 51.9 |  | Minimum of: APC Setpoint + ∆MW and 95% of AAP + ∆MW1, 2
|  | FD | f = 51.9 | PD | Minimum of: APC Setpoint and AAP and DMOL
|  | FE | f = 52 | PE | 0%3
|  |  | f > 52 |  | 0%3
Minimum reserve level in Curve 2 is 5% of Available Active Power, not lower than DMOL (settable between DMOL and 100%)
Frequency Response Mode OFF
Curve 1 and Curve 2: Wind Following Mode
|  |  | Transmission System Frequency (Hz) |  | Required Active Power Output
|  |  | 47.5 ≤ f ≥ 52 | No governor action | 100% of AAP
Curve 1 and Curve 2: Active Power Control Mode
|  |  | Transmission System Frequency (Hz) |  | Required Active Power Output
|  |  | 47.5 ≤ f ≥ 52 | No governor action | Minimum of: AAP and APC Setpoint
1 APC Setpoint + ∆MW shall have a lower limit of the minimum of: APC Setpoint and DMOL.
2 (95% of) AAP + ∆MW shall have a lower limit of the minimum of AAP and DMOL
3 Any WTG which has disconnected due to high frequency shall be brought back on load as fast as technically feasible, provided the Frequency has fallen below 50.2Hz.
DMOL shall not be greater than 12% of Registered Capacity
If AAP < DMOL and f < FE, maximise output
Ramp Rates:
|  | Mode | Rate | Priority | Comment
|  | Frequency Response | As fast as technically possible. 60% of its expected Active Power response within 5 seconds 100% of its expected Active Power response within 15 seconds. | 1
|  | Active Power Dispatch | 20% of Registered Capacity per Minute | 2 | Settable between: 1-100% Registered Capacity per Minute
|  | Wind Following | 20% of Registered Capacity per Minute | 3 | Settable between: 1-100% Registered Capacity per Minute
Frequency Droop:
|  | Frequency Droop | Droop Calculation | Comment
|  | 4% |  | Settable between: 2-10%, online
Rate of Change of Frequency:
If possible, ROCOF should be disabled on Transmission System-connected Windfarms. If this is not possible, ROCOF should be set to max that machine is capable of. Under no circumstances should ROCOF be set to less than 0.5 Hz/s
Proposed Modification to Grid Code. (Ref#MPID 229).
Voltage Regulation System Slope Setting
|  | Voltage System Slope | Voltage Calculation | Comment
|  | 4% |  | 90% of steady State Reactive Power response within 1 second including transition from maximum Mvar production to maximum Mvar absorption or vice-versa.
Note. Frequency Response settings have been updated to clarify expected performance below DMOL - per feedback from industry. Changes are highlighted in red.
Note. Fd and Fe have been updated, along with clarification of minimum reserve held. Changes are highlighted in red.

## Turbine Protection Settings
Recommended Wind Farm Power Station (WFPS) Turbine Protection Settings to be applied by WFPS
| Underfrequency stage 1 Setpoint | f< | 47.5 Hz | If only two stages available for underfrequency on relay, use stage 2 and stage 3
| Underfrequency stage 1 time delay | t< | 3600 s
| Underfrequency stage 2 Setpoint | f<< | 47.4 Hz
| Underfrequency stage 2 time delay | t<< | 20 s
| Underfrequency stage 3 Setpoint | f<<< | 46.9 Hz
| Underfrequency stage 3 time delay | t<<< | 1 s
| Overfrequency stage 1 Setpoint | f> | 52Hz
| Overfrequency stage 1 time delay | t> | 3600 s
| Overfrequency stage 2 Setpoint | f>> | 52.1 Hz
| Overfrequency stage 2 time delay | t>> | 1 s
| Rate of Change of Frequency setpoint | df/dt | Max | If possible, ROCOF should be disabled on Transmission System-connected Windfarms. If this is not possible, ROCOF should be set to max that machine is capable of. Under no circumstances should ROCOF be set to less than 1 Hz/s over 500 ms
| Rate of Change of Frequency delay | t | Max
| Undervoltage stage 1 Setpoint | U< | 0.89 pu
| Undervoltage stage 1 time delay | t< | 3 s
| Undervoltage stage 2 Setpoint | U<< | 0.14 pu
| Undervoltage stage 2 time delay | t<< | 0.625 s
| Overvoltage stage 1 Setpoint | U> | 1.11 pu
| Overvoltage stage 1 time delay | t> | 60 s | This is the minimum time delay we would recommend. If the plant can operate at this voltage for longer periods, then a longer time delay (at the discretion of the WFPS) should be implemented.
| Overvoltage stage 2 Setpoint | U>> | 1.2 pu
| Overvoltage stage 2 time delay | t>> | 15 s | This is the minimum time delay we would recommend. If the plant can operate at this voltage for longer periods, then a longer time delay (at the discretion of the WFPS) should be implemented.
| Fault Ride Through Events | N | N/A | Trip & Lockout Settings. i.e No. of events within specified time period. Confirm if time period is rolling. NB. Lockout is not recommended by EirGrid.
| Fault Ride Though Time Period (Rolling) | t | N/A

## Test Schedule and Templates
Grid Code Compliance Test Schedule and Test Procedure templates
SCHEDULE OF GRID CODE COMPLIANCE TESTS
http://www.eirgridgroup.com/site-files/library/EirGrid/WFPS_Schedule_of_GridCodeComplianceTests.xlsx
Test Procedure Templates
http://www.eirgridgroup.com/site-files/library/EirGrid/WFPS_TestProcedureActivePowerControl.docx
http://www.eirgridgroup.com/site-files/library/EirGrid/WFPS_TestProcedureBlackStartShutdown.docx
http://www.eirgridgroup.com/site-files/library/EirGrid/WFPS_TestProcedureFrequencyResponse.docx
http://www.eirgridgroup.com/site-files/library/EirGrid/WFPS_TestProcedureReactivePowerCapability.docx
http://www.eirgridgroup.com/site-files/library/EirGrid/WFPS_TestProcedureReactivePowerControl.docx