## Derogation Register
ID | Granted | Until | Status | Change? | Extension Ref | Generator Name | Responsible Party | Explanation | Why Derogaration Granted | Grid Code Section and Clause | Grid Code Version | Notes
11 | 2006-03-31 | Enduring | Active |  |  | Coolkeeragh | ESB | Minimum generation level | New minimum generation level granted and new requirements on data provision, operation in OCGT mode | Condition 4 pagraph 2
12 | 2006-11-28 | Enduring | Active |  |  | Callagheen | CRE Energy Ltd | Fault Ride Through, Neg Phase Sequence Loadings, Voltage Control | While not meeting code, NIE found Fault ride through to be acceptable | CC.S2.3.6(d)
12 | 2006-11-28 | Enduring | Active |  |  | Callagheen | CRE Energy Ltd | Negitive Phase Sequence Loadings | While not meeting code, NIE found Neg Phase Sequence Loadings allowed as not initial requirement setting | CC.S2.3.7
12 | 2006-11-28 | Enduring | Active |  |  | Callagheen | CRE Energy Ltd | Voltage Control | Voltage control at 33kV busbar | CC.S2.5.3(d)
36 | 2008-11-01 | Enduring | Active |  |  | Garves | Garves Wind Farm | WFPS Reactive Power capacbility | Reactive power capability shall be absorbing 0.95 and generating 0.98 from the connection point | CC.S2.3.2
36 | 2010-02-01 | 2011-01-31 | Expired |  |  | Kilroot | AES Power Ltd | Spinning Reserve Capability | Only generators with PPA CDGU to notify TSO with a Sustained reposnse Capacility figure if not able to meet Spinning reserve Capability | SDC1.B.4.2 |  | 1 Direction separated out into each company
36 | 2010-02-01 | 2011-01-31 | Expired |  |  | Ballylumford | Premier Power Ltd | Spinning Reserve Capability | Only generators with PPA CDGU to notify TSO with a Sustained reposnse Capacility figure if not able to meet Spinning reserve Capability | SDC1.B.4.2 |  | 1 Direction separated out into each company
36 | 2010-02-01 | 2011-01-31 | Expired |  |  | Coolkeeragh | Coolkeeragh ESB Ltd | Spinning Reserve Capability | Only generators with PPA CDGU to notify TSO with a Sustained reposnse Capacility figure if not able to meet Spinning reserve Capability | SDC1.B.4.2 |  | 1 Direction separated out into each company
49 | 2011-08-23 | 2012-08-23 | Expired |  |  | Altahullion II | Althahullion II | WFPS Control Arrangements | Additional Control loop must be provided to ensure oscillations between 0.25 and 1.75Hz. Total peak to peak oscillation should be less than 10 of dispatchable WFPS | CC.S2.2.5.3
35 | 2011-08-23 | 2012-08-23 | Expired |  |  | Lough Hill | Lough Hill Wind Farm Power Station | WFPS Control Arrangements | Additional Control loop must be provided to ensure oscillations between 0.25 and 1.75Hz. Total peak to peak oscillation should be less than 10 of dispatchable WFPS | CC.S2.2.5.3
41 | 2012-06-01 | Enduring | Active |  |  | Slieve Kirk | SSE | Reactive Capability | Ambiguous requirement within 'current' grid code. SONI aggrees on the acceptable performance for this requirement | CC.S2.1.5.3 Part (a)
42 | 2013-12-11 | 2014-03-14 | Expired |  |  | Slieve Kirk | SSE | Reactive Power - temporary to alllow for installation on Cap Bank | Capacitor bank must be installed onsite to be compliant - expected to be completed in Feb 2013 | CC.S2.1.3.2
45 | 2014-12-01 | 2015-03-31 | Expired |  |  | Carrickatane | Hunters Hill Wind Farm Ltd | Transducer Failure | Work required at site to upgrade software to existing Wind Farm Control System | WFPS 6.4.1.3 | 2013-10-01
43 | 2014-12-01 | 2015-02-27 | Expired |  |  | Slieve Kirk | SSE | New installation of Voltage Control Method | SSE install and testing required | CC.S2.1.5.3 Part (a) | 2013-10-01 | Temporary derogation
51 (WM031-11-70) | 2015-02-27 | 2015-07-31 | Expired |  |  | Dunmore | Sgurr Energy | Lack of Transducer Alarm | Incorrect implementation of maximum instantenous output within windfarm control system | WFPS 6.4.1.3 | 2013-10-01
39 | 2015-04-15 | Enduring | Active |  |  | Bessy Bell 2 | SSE | Magnitude of frequency reserve response incorrectly implemented | Unclear definition of maximum instantenous output at time of energisation | CC.S2.2.5.2
40 (Ref: WM031-11-074 | 2015-04-15 | Enduring | Active |  |  | Bin Mountain |  | Magnitude of frequency reserve response incorrectly implemented | Due to unclear definition of maximum instantenous output at time of energisation | CC.S2.2.5.2(b) | 2013-10-01
46 & CNO/E/TH265 EXT | 2015-05-11 | 2017-05-11 | Active |  | CNO/E/TH265 | Lisahally Biomass | ERE | Min Gen derogated to 70% and changes to start up and ramp rates | Generator unable to comply with start up and ramp rates due to restrictions on technology and temperature restrictions. | CC.S1.2.3.7
53 CNO/E/TH/087 | 2016-10-17 | Enduring | Active |  |  | Thornog | Thornog Wind Farm Ltd | WFPS Control System Tests - no requirment to hold last known setpoint for 10 minutes in the event of a failure scenario | Relatively small active power export capacity and probablility of failure is very low | WFPS Settings Schedule Section 6.4
54 CNO/E/TH/093 | 2016-10-26 | Enduring | Active |  |  | Slieve Rushen | Mantlin Ltd | Grid Code Derogation WFPS Control Arrangements | Substantial benefits to moving onto new configuration | Distribution Code (2010) Condition 7.4 and WFPS Setting Schedule v5.
55 | 2017-03-23 | 2022-03-31 | Expired | Y |  | Coolkeeragh | ESB | Request to change POR of 45MW to 38MW | CESB believe the technical capacility of the plant is 38MW | GD2(xiii)© | 2015-08-01
56 CNO/E/TH/179 | 2017-05-09 | 2017-11-09 | Expired |  |  | Thornog | Thornog Wind Farm Ltd | Change of amount of time last stpoint should be held in event of communications failure | Short period of derogation to complete the fix and coordinate and carry out testing | CC.S2.2.5.2(b)
57 (CNO/E/TH/213) | 2017-08-04 | 2024-12-31 | Active |  |  | Kilroot | AES | Start-up and Ramp Rates - Warm up time set to 6 hours (GC allows 5) | No affect to system security, no material impacts on consmer costs, maximises plant lifetime | CC.S1.2.3.4(a)(ii) |  | Direction applied to 31st Dec 24 as plant forecast to close
58 CNO/E/TH/253 | 2017-11-08 | 2018-02-09 | Expired |  |  | Thornog | Thornog Wind Farm Ltd | Extension to 58 CNO/E/TH/253 | Testing still outstanding - weather dependant | CC.S2.2.5(b)
CNO/E/TH256 | 2017-11-17 | 2018-05-11 | Expired |  |  | Lisahally Biomass | ERE | Min Gen derogated to 70% and changes to start up and ramp rates | Generator unable to comply with start up and ramp rates due to restrictions on technology and temperature restrictions. | CC.S1.3.7
59 | 2018-01-18 | 2022-03-31 | Expired | Y |  | Coolkeeragh | ESB | In realtion to the decrement rate POR value of 1:1 for CESB Gernerator C30 | CESB states decrement rate of 0.67 is required to reflect the capability of C30. | GD2: (xiii)© | 2015-08-01 | Requested Lifetime derogation but is to be reviewed every 5 years
64 NET/E/TH/30 | 2018-11-12 | 2028-11-30 | Active |  |  | Lisahally Biomass | ERE | Must be capable of remaining synchronised to the grid at an output no greater than 70% of MCR. Must comply with a ramping up/de-loading rate of 2.4MW/h | GHD feel biomas would not allow the Grid Code's required 40% of MCR. Granted until expected end of life of plant | CC.S1.2.3.3 and CC.S1.2.3.4
60 (NET/E/TH/23) | 2018-11-15 | 2019-11-15 | Expired |  |  | Ballylumford | AES | Removes SONI facility to view variations in CT accuracy. SONI will instead check metering from Unit B21 via SCADA monthly | CT replacement | Metering Code Sub-Code NO. 2.1, section 3.3.5(a) and 3.3.5(e)
NET/E/TH/54 | 2019-01-31 | 2022-02-01 | Expired | Y |  | Kilroot | AES | Power Factor of 0.85 lagging allowed soley to combined K1, GT1 and K2,GT2 connection Points for specific circumstance of revelant GT operating at full load and main unit is dispaptched above 242MW | Possilbility to increase capability of boilers K1 and K2 and prvoide additional 20MW of generated electrical power | CC.S1.1.3.2.(i)
NET/E/TH/154 | 2019-10-22 | 2020-11-15 | Expired |  |  | Ballylumford | EPB | Extension to 60 (NET/E/TH/23) | Delay to delivery of replacements CTs to site until August 2019. Request to do work during scheduled shutdown, so request to do so in GT21 major overhall in Q3 2020 | Metering Code Sub-Code NO. 2.1, section 3.3.5(a) and 3.3.5(e)
NET/E/TH/226 | 2020-06-19 | 2022-04-01 | Expired | Y |  | Coolkeeragh | ESB | Replaces 2017 degrogations | Replaces 2017 derogations | CC.S1.1.3.8, SDC3.4.1.1(s), SDC3.6.1 and SDC1.4.8.10
NET/E/JF/402 | 2021-06-25 |  | Active |  |  | Kilroot KT7 | EPKL | Want to reduce the minimum generation requirement while remaining synchronised to NI system as KTG7 cannot remain synchronsised at 140MW (40% of registered capacity) therefore also not 80MW | Allows SONI more flexibility for more efficient and econmomical operation of System and possibilty reduce curtailment of renewables. 36 month long enough for research and analysis around min gen requirements in Grid Code | CC.S1.1.3.8 | 2020-10-01 | Valid for 36 months from the date that SONI and EPKL enter into GTUoS Agreement
37 | ?? No docs | 2010-02-01 | Expired |  |  | Hunters Hill Wind Farm | ESB
48 | Was this approved? |  |  |  |  | Full Circle Generation | Full Circle Generation Ltd | Request to be considered as Independent Generating Units instead of Centrally Dispatchable Generating Units | Desire to datisfy threshold parameters as advised to FCG and BA at onset of projet: Non-participation in SEM; Avoidance Central Dispatch; Minimise TUOS Charges | Removed from DG13 and added to GD27
48 | Was this approved? |  |  |  |  | Bombardier Aerospace | Full Circle Generation Ltd | Request to be considered as Independent Generating Units instead of Centrally Dispatchable Generating Units | Desire to datisfy threshold parameters as advised to FCG and BA at onset of projet: Non-participation in SEM; Avoidance Central Dispatch; Minimise TUOS Charges | Removed from DG13 and added to GD27
NET/E/JF/401 | 2021-06-25 |  | Active |  |  | Kilroot KTG6 | EPKL | Want to reduce the minimum generation requirement while remaining synchronised to NI system as KTG6 cannot remain synchronsised at 140MW (40% of registered capacity) therefore also not 80MW | Allows SONI more flexibility for more efficient and econmomical operation of System and possibilty reduce curtailment of renewables. 36 month long enough for research and analysis around min gen requirements in Grid Code | CC.S1.1.3.8 | 2020-10-01 | Valid for 36 months from the date that SONI and EPKL enter into GTUoS Agreement
52 | 2021-06-26 |  |  |  |  | Fair Head Tidal |  | NI Grid code requirements of 0.33 p.u. reactive power leading and lagging at full active power output. Less than 5MW therefore falls outside the grid code although if it wants to increase capacity it will have to comply
NET/E/JF/555 | 2022-08-08 | 2023-09-30 | Active |  |  | Kilroot Unit K1 & KGT1 | EPKL | Rated power factor unable to be minimum 0.8 | Known issue which has previously been derogated. | CC.S1.1.3.2
NET/E/JF/554 | 2022-08-08 | 2023-09-30 | Active |  |  | Kilroot Unit K2 & KGT2 | EPKL | Rated power factor unable to be minimum 0.8 | Known issue which has previously been derogated. | CC.S1.1.3.2 |  | Derogation granted for lifetime of units
2021-06-29
2021-06-30
2021-07-01
2021-07-02
2021-07-03
2021-07-04
2021-07-05
2021-07-06
2021-07-07
2021-07-08
2021-07-09
2021-07-10
2021-07-11
2021-07-12
2021-07-13
2021-07-14
2021-07-15
2021-07-16
2021-07-17
2021-07-18
2021-07-19
2021-07-20
2021-07-21
2021-07-22
2021-07-23
2021-07-24
2021-07-25
2021-07-26
2021-07-27
2021-07-28
2021-07-29
2021-07-30
2021-07-31
2021-08-01
03_2023_01 | 2023-12-21 | Enduring | Active |  |  | Kilroot Unit KGT3 & KGT4 | EPUKI | Rated power factor unable to be minimum 0.8 as it is required in CCS1.1.3.2 |  | CC.S1.1.3.2 |  | Derogation granted for lifetime of units
11_2023_01 | 2023-12-21 | Enduring | Active |  |  | Kilroot KGT3 & KGT4 | SONI | Matching derogation to the above Derogation 03_2023_01 | Known issue which has previously been derogated. | CC.S1.1.3.2 |  | Matching derogation to the above
05_2023_01 | TBC |  | In Progress |  |  | Kilroot Unit KG6 & KGT7 | EPNIE | Want to reduce the minimum generation requirement while remaining synchronised to NI system as KTG6 cannot remain synchronsised at 140MW (40% of registered capacity) therefore also not 80MW | Known issue which has previously been derogated. | CC.S1.1.3.8 |  | Same derogation as NET/E/JF/401 butg new owner
07_2023_01 | TBC |  | In Progress |  |  | Kilroot Unit KG6 & KGT7 | SONI | Matching derogation to Derogation 05_2023_01 |  | CC.S1.1.3.8 |  | Matching derogation to the derogation above
09_2023_01 | TBC |  | In Progress |  |  | Kilroot Unit KGT6 and KGT7 | EPNIE | Generators have a slower than required ramp rate between 326MW and 350MW than is required in OC3.4.2.2 which means that the generators cannot provide reserve between 326MW and 350MW as is reqired in CC.S1.1.3.9 |  | CCS1.1.3.9 & OC3.4.2.2
05_2022_01 | 2024-03-20 |  | Active |  |  | Coolkeeragh Unit C30 | ESB | Replaces 2020 Minimyum Generation Derogation CC.S1.1.3.8 | Replaces 2020 Derogation | CC.S1.1.3.8
12_2023_01 | 2024-03-20 |  | Active |  |  | Coolkeeragh Unit C30 | SONI | Matching derogation for the above Derogation 05_2022_01 | Replaces 2020 Derogation | CC.S1.1.3.8 |  | Matching derogation to the derogation above
10_2023_01 | TBC |  | In Progress |  |  | Contour GlobalAGU | ContourGlobal Solutions | Derogation to minimum notice for closedown requitred |  | PC6.1.6