## Cover Sheet
UNIT NAME Grid Code Compliance Progress Summary
Disclaimer:
This document contains information (and/or attachments) which may be privileged or confidential. All content is intended solely for the use of the individual or entity to whom it is addressed. If you are not the intended recipient please be aware that any disclosure, copying, distribution or use of the contents of this document is prohibited. If you suspect that you have received this document in error please notify SONI immediately. Further information can be found at: https://www.soni.ltd.uk/legal/ It is recommended that a Generator make contact with SONI at an early stage of the project, prior to signing a contract with Generating Unit manufacturers. SONI will provide guidance on technical issues and plant performance requirements. At all times SONI must be in possession of an up-to-date full and accurate parameter listing of the Generating Unit. This parameter listing must cover all operational control functionality including Frequency, voltage and all the Generating Unit parameters relating the control and operation of the Generating Unit. Should this parameter listing change at any stage, the Generator must reissue the revised parameter listing to SONI. There should be no prior modification of control parameters until they have been agreed with SONI.
It is recommended that a Generator make contact with SONI at an early stage of the project, prior to signing a contract with Generating Unit manufacturers. SONI will provide guidance on technical issues and plant performance requirements. At all times SONI must be in possession of an up-to-date full and accurate parameter listing of the Generating Unit. This parameter listing must cover all operational control functionality including Frequency, voltage and all the Generating Unit parameters relating the control and operation of the Generating Unit. Should this parameter listing change at any stage, the Generator must reissue the revised parameter listing to SONI. There should be no prior modification of control parameters until they have been agreed with SONI.

## TEST PROVISIONS
SONI General Provisions Applicable to all Test Procedures
1- Generating facility shall inform SONI of the planned and scheduled tests for compliance verification. (Art 40-4)
2- The planned test schedule shall be approved by SONI in a timely manner prior to the commencement of such test. (Art 40-4)
3 - SONI may choose to participate in the compliance testing either on site or remotely from its control centre (Art 42-4)
4 - Generating facility is responsible for recording all relevant test signal. However, for each test, signals as specified by SONI will be made available to SONI for recording separately if required (Art 42-4)
5 - SONI shall inform the generating facility of the test outcome (Art 41-1)
6 - SONI may ask for compliance tests or simulations to be repeated following any failure, modification, or replacement of any equipment (Art41-2)
7 - Generating facility shall provide the following documents and technical data as part of the testing compliance procedures (Art 41-3-a and b)
8 - SONI shall not (or shall) accept an alternative set of test to those given as part of this compliance procedure (Art 42-2-a)
9 - SONI may require additional or alternative sets of tests to those give in this procedure when deemed insufficient to demonstrate compliance (Art 42-2-b)
10 - SONI may require appropriate tests when the generating facility is operating on alternative fuels or fuel mixes (Art 42-2-c)
11 - SONI shall not (or shall) accept provision of equipment certificates submitted as part of demonstrating compliance with relevant test requirement (Art 44-1, 46-2, 48-1 and 49-2)

## Version Control
Version Control
Version | Date | Written by: | Reviewed by: | Approved by: | Description of changes | Change requested by
0.1 | 2021-04-27 | D McSwiggan |  |  | first issue | internal

## Scope of Works
Scope of Works
Outline the scope of the works required e.g.
New Unit
or
Governor refurbishment
MV switch gear replacement
etc.

## Progress Summary
XX1 Status XXth XXXXX 20XX
|  | %Test procedures agreed | % Performed on Primary Fuel | % Performed on Secondary Fuel | % Closed
| EON |  |  |  | 0%
| ION | 0% |  |  | 0%
| FON | 0% | 0% | 0% | 0%
| System Tests | 0% | 0% |  | 0%
| Update provided | Backfeed of Connection Transformer | Synchronisation of Unit (first export) | Start of High Export | Operational Certification
Current schedule
N-1 schedule
N-2 scheulde
EON | Description | Test Status
1 | Provision of Requirements | Open
#REF! | #REF! | #REF!
3 | Modes of Operation | Open
4 | Protection Settings | Open
5 | Governor Data | Open
6 | Excitation System & Generator | Open
7 | Transformer | Open
8 | Transformer Oil Test | Open
9 | Interface Cabling Scheme | Open
10 | Earthing & Lightning Protection | Open
11 | Power Station CT's & VT's | Open
12 | Function and accuracy check of protection | Open
13 | Operation & Interlocking Check | Open
14 | Interface Cabling Checks | Open
15 | Metering Equipment | Open
16 | Insulation resistance tests | Open
17 | Resistance test for connections. | Open
18 | Authorisation to Construct | Open
19 | Unit Registration | Open
20 | Operational Information | Open
21 | Operation Instruction & Standard Operating Procedure | Open
22 | Declaration of Fitness | Open
23 | Energisation Instruction | Open
24 | Isolation for Energisation | Open
ION | Description | Test procedure agreed | Test Status Primary Fuel
25 | Energise transformer | Open | Open
26 | Insulation Resistance Tests | Open | Open
27 | Resistance test for connections. | Open | Open
28 | Function and accuracy check of protection | Open | Open
29 | Signal Interface | Open | Open
30 | Generator Excitation - offline checks | Open | Open
31 | Function Check of protection alarm | Open | Open
32 | Function check of signals | Open | Open
33 | Turbine overspeed test. | Open | Open
34 | Generator Governor - offline checks | Open | Open
35 | Synchroniser Checks | Open | Open
36 | Declarations of Fitness | Open | Open
FON | Description | Test procedure Agreed | Testing Completed on Primary Fuel | Testing Completed on Secondary Fuel | Test Status
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
40 | Frequency Response (Governor Droop) | Open | Open | Open | Open
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
44 | Full Load Rejection followed by Islanded Mode (Trip to House Load) | Open | Open | Open | Open
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
50 | Reactive Power Capability (Excitation Limiters) | Open | Open | N/A | Open
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
#REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Phase D | Description | Test procedure Agreed | Testing Completed on Primary Fuel | Testing Completed on Secondary Fuel | Test Status
67 | Black Start | Open | Open | Open | Open
68 | Operating Reserves | Open | Open | Open | Open
69 | Ramping Margins | Open | Open | Open | Open
70 | Fast Post Fault Active Power Recovery & Dynamic Reactive Response | Open | Open | Open | Open
71 | Steady State Reactive Power | Open | Open | Open | Open
72 | Synchronous Inertial Response | Open | Open | Open | Open

## Issues Log
No. | Issue Description | Owner | Action | Decision | Status
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
The Issues Log shall be populated with any items that are identified outside of the prescribed tests, identified following the closure of a prescribed test, or during performance monitoring of the unit, prior to issuance of an Operational Certificate. All items in the Issues Log shall be closed prior to the issuance of an Operational Certificate.

## EON
Test # | Test | Grid Code Reference | SONI Witness | Description | Comment | Status
1 | Provision of Requirements |  | No | SONI shall provide the customer with: - RoCoF assessment pack with the MSS data. - FRT report template. - Harmonics pack - Signal List, based on SLD - Template for incident reports - Specification and process for system alerts - Specification for AGC |  | Open
3 | Modes of Operation |  | No | Where relevant (e.g. combined cycle plant), the unit shall provide a description of different plant configurations (e.g. combustion turbine and steam turbine configurations). Note this will inform the testing required in FON. |  | Open
4 | Protection Settings | CC6.4.1 to CC6.10 | No | The unit shall agree the following protection settings with SONI: - generator - generator transformer(s) - unit transformer(s) - balance of plant Generator transformer shall have differential and buchholz protection and the unit transformer shall have overcurrent (HV side preferable), differential and buchholz protection for first energisation |  | Open
5 | Governor Data |  | No | The unit shall provide the following for the Governor System: - design sheets - settings list - FAT results The unit shall provide conversion charts for plant output for variations with ambient conditions |  | Open
6 | Excitation System & Generator | CC.S1.1.3.2, CC.S1.1.3.3, CC.S1.1.5.3 | No | The unit shall provide the following for the Excitation System: - data sheets - settings list - FAT results The unit shall provide the Generator data sheets |  | Open
7 | Transformer | CC.S1.1.3.5 | No | The unit shall provide the following for the Generator Transformer: - as built data sheet - legible photograph of transformer Name Plate Rating - FAT results of including transformer impedance data (positive and zero phase sequence) for top centre and bottom tap positions. The unit shall provide the following for the Unit Transformer: - as built data sheet - legible photograph of transformer Name Plate Rating - FAT results of including transformer impedance data (positive and zero phase sequence) for top centre and bottom tap positions. |  | Open
8 | Transformer Oil Test |  |  | The unit shall provide on-site oil test results (moisture content and gas breakdown) for the Generator Transformer and Station/Unit Transformer. | Test is carried out with the transformer on site Pass/Fail is required with test results or statement that results are acceptable to the customer. | Open
9 | Interface Cabling Scheme | CC8.4 | May be Wittnessed by SONI | The unit shall submit the following for review: - Inter-tripping schemes, - Interlocking schemes - SCADA signal schemes Check that proposed interlocking for Power Station fits in with SONI specification. |  | Open
10 | Earthing & Lightning Protection | CC6.8 | No Yes | The unit shall provide an inspection report confirming Power Station earthing and lightning protection system is complete for transformers and generator. The unit shall provide an inspection report confirming connection between Power Station earth grid and Transmission Station earth grid is complete (this will include earth resistance measurements) |  | Open
11 | Power Station CT's & VT's | CC5 | No | The unit shall provide FAT & SAT results for all CT's & VT's on: - Generator bus ducts - MV incomer - Generator transformer - Unit transformer Confirm CT’s & VT's are suitable for function and keep a record of as-built characteristic. |  | Open
12 | Function and accuracy check of protection | CC6.4 | No | The unit shall provide SAT results and commissioning documentation for function and accuracy check of all protection for: - generator - generator transformer - unit transformer - balance of plant including secondary cabling, by secondary current and voltage injection. Except for functions that have to be tested with the generator running |  | Open
13 | Operation & Interlocking Check | PC.A3.1.2 | No | Check operation and interlocking for: - HV CB - HV Disconnect - HV Earth Switch - Generator CB - Generator Disconnect - Generator CB Earth Switch - MV CB - MV Earth Switch |  | Open
14 | Interface Cabling Checks | CC8.4 | May be Wittnessed by SONI | The unit shall provide SAT and commissioning documentation for function check of all trip commands, signals and alarms: - from Transmission Station to Power Station - from Power Station to Transmission Station - Check of all signals to the units SCADA system. Test carried out in co-operation with SONI subcontract including actual tripping of HV CB by emergency trip pushbutton |  | Open
15 | Metering Equipment | CC6.3 | May be Wittnessed by SONI | Check, calibration and sealing of Transmission Station metering including signals to Power Station. NIEN (Metering Services) to provide DoF for revenue metering as part of Energisation Instruction. |  | Open
16 | Insulation resistance tests |  | No | The unit shall provide the SAT results for insulation resistance tests of: - generator transformer HV and LV sides - unit transformer HV and LV sides - all MV apparatus being energised Check that all plant to be energised is in a fit state to be energised by doing an insulation measurement test or HV test as appropriate. |  | Open
17 | Resistance test for connections. |  | No | The unit shall provide the SAT results for resistance tests of connections installed following completion of insulation tests. Verify that connections of flexibles will carry the full load current. May be a combination of torque on the bolts and measurement of the resistance of the connections. |  | Open
18 | Authorisation to Construct |  |  | e-mail licensing@cru.ie (cc to Generator_Testing@SONI.com) requesting confirmation of consented MW capacity |  | Open
19 | Unit Registration |  | No | The unit must be registered in the market before energistaion. In order to register in the market, the unit must: - submit a fully completed party accession pack - submit a fully completed particpant notification pack The unit must be registered in EDIL before energisation. - submit a completed EDIL registration form - carry out EDIL training Deadline: 60 days before energisation |  | Open
20 | Operational Information |  |  | Provide the following to SONI Customer Relations via e-mail to info@SONI.com - 24 hour contacts - Authorised Operators - Authorised DOF givers Note. Authorised Operators must be agreed and trained with NIEN for switching to take place. |  | Open
21 | Operation Instruction & Standard Operating Procedure | CC6.2.3 | No | Agree Operating Instruction, including a check to see that the procedures can be safely followed. Written by SONI, agreed with NIEN and the unit. Suitable operating personnel are available with call-out procedure that is in line with SONI Operating Instruction. The unit shall provide the Standard Operating Procedure which covers the following scenarios: - tripping of generator - failure of protection - failure of power supplies etc. |  | Open
22 | Declaration of Fitness |  | N/A | The unit shall issue Declarations of Fitness as specified in the Energisation Instruction. |  | Open
23 | Energisation Instruction |  | May be Wittnessed by SONI | Agree Energisation Instruction for 1st energisation of the connection point. Undertaken by SONI CHCC. |  | Open
24 | Isolation for Energisation | Safety Procedures | May be Wittnessed by SONI | Check secondary side and neutral connection of generator and unit transformer is completed up to suitable isolating points and that secondary VT neutral point is connected and earthed. Check that suitable (lockable) earthing facilities are available for the equipment on the other side of the isolating points. Check access for visual check of earth switch and isolators |  | Open
2 | Provision of Studies & Model | CC15.1 | No | The following simulation studies shall be provided: - Fault Ride Through - Limited Frequency Sensitive Mode - overfrequency - Limited Frequency Sensitive Mode - overfrequency - Frequency Sensitive Mode - Load Rejection/Islanding - Reactive Capability - Power System Stabiliser/Damping | PROVIDE A LINK TO SIMULATIONS PROCEDURE | OPEN
All tests to be completed to achieve Energisation Operational Notification
Key
RfG Requirements
Non-Rfg Requirements
Note on C1: SONI TSO: The following Grid Code references are not intended to be exhaustive rather they are intended to provide high-level guidance for specifing the minimum technical, design and certain operational criteria which must be complied with by Users connected to or seeking connection with the Transmission System. Users seeking connection to the Transmission System wil be required to comply with all applicable Grid Code requirements.

## ION
Test # | Test | Document Name | Grid Code Reference | EirGrid Witness | Description | Comment | Test procedure Agreed | Test Status
1 | Provision of Updated Studies & Model |  | CC15.1 | No | The following simulation studies shall be provided: - Fault Ride Through - Limited Frequency Sensitive Mode - overfrequency - Limited Frequency Sensitive Mode - overfrequency - Frequency Sensitive Mode - Load Rejection/Islanding - Reactive Capability - Power System Stabiliser/Damping | PROVIDE A LINK TO SIMULATIONS PROCEDURE
25 | Energise transformer |  |  | Yes | Energise the connection point per agreed Energisation Instruction |  | Open | Open
26 | Insulation Resistance Tests |  |  | No | The unit shall provide SAT results for insulation resistance tests of: - MV cables / IPBs / switchgear that was not tested in phase A - generator stator Check that all plant to be energised is in a fit state to be energised by doing an insulation measurement test or HV test as appropriate. |  | Open | Open
27 | Resistance test for connections. |  |  | No | The unit shall provide the SAT results for resistance tests of connections on IPB flexibles following installation and completion of insulation tests. Verify that connections of flexibles will carry the full load current. May be a combination of torque on the bolts and measurement of the resistance of the connections. |  | Open | Open
28 | Function and accuracy check of protection |  | CC 10 | No | The unit shall provide SAT results and commissioning documentation for function and accuracy check of all protection that was not tested in phase A. Including secondary cabling, by secondary current and voltage injection. Except for functions that have to be tested with the generator running |  | Open | Open
29 | Signal Interface |  | CC 7.2.3 & CC 10 & CC12 | Yes | Function check of all Transmission Station trip commands and signals and alarms/recording: - from Transmission Station to Power Station - from Power Station to Transmission Station - from interface/NCC to SCADA system. Check actual tripping of HV CB by emergency trip pushbutton Note that some or all of these tests may already have been completed in Phase A tests. |  | Open | Open
30 | Generator Excitation - offline checks |  |  | Yes | Open Circuit and Short Circuit testing Verification of Xd and Short Circuit Ratio. CC7.3.1.1 (j) states that the short circuit ration of each Generation Unit shall be in accordance with IEC 60034 Functional checks of Excitation control (e.g. AVR stationer and dynamic control checks at no load condition) |  | Open | Open
31 | Function Check of protection alarm |  |  | Yes | Function Check of protection alarm by primary voltage and current injection during open and short circuit tests. |  | Open | Open
32 | Function check of signals |  |  | Yes | Function check of signal transmitters by primary voltage and current injection during open and short circuit tests. |  | Open | Open
33 | Turbine overspeed test. |  |  | No | Demonstrate operation of all turbine overspeed protection. |  | Open | Open
34 | Generator Governor - offline checks |  |  | Yes | Testing of Governor system - Functional checks (governor stationer and dynamic control checks at no load condition) |  | Open | Open
35 | Synchroniser Checks |  | CC 7.3.3 & CC 7.3.4 | Yes | Testing of synchroniser - Generator CB and check contact closing time. Test protocols of factory tests to be available. Testing of synchroniser by backfeeding to generator to check VTs and then by testing pulses to blocked generator CB during dummy synchroniser tests using high speed recorder. CC7.3.4 The synchronising facilities in CC7.3.3 shall facilitate synchronising under (a) frequency between 48-52 Hz and voltage between 99 kV-123 kV. |  | Open | Open
36 | Declarations of Fitness | Declaration of Fitness | CC 7.3.3 & CC 7.3.4 | N/A | Power Station to issue Declaration of Fitness Market Registration is completed Load Profiles for export have been approved by the TSO and SEM |  | Open | Open | New Link Required
All tests to be completed to achieve Interim Operational Notification
Key
RfG Requirements
Non-Rfg Requirements
Note on C3: Zia Emin: All rows filled with RED colour need checking by SONI personnel whether they should remain here as part of the compliance checks. Those that are remaining will require cross referencing to the right clause within SONI Grid Code.

## FON
Test # | Test | Document Name | SONI Grid Code Reference | SONI Witness | Description | Comment | Test procedure Agreed | Testing Completed on Primary Fuel | Testing Completed on Secondary Fuel | Test Status | Link to template procedure on website (Update all links!!)
| Provision of Updated Studies & Model |  | CC15.1 |  | The simulation/model report of EON stage will be updated to provide validation of the submitted model for the following studies. Validation shall be perfored against the actual test results from FON stage: - Limited Frequency Sensitive Mode - overfrequency - Limited Frequency Sensitive Mode - overfrequency - Frequency Sensitive Mode - Reactive Capability | [5 empty] | PROVIDE A LINK TO SIMULATIONS PROCEDURE
44 | Full Load Rejection followed by Islanded Mode (Trip to House Load) | Full Load Rejection followed by Island Mode Operation | OC7.5.4 | Yes | Load rejection test at 100% load and resynchronisation across HV CB after 4 hours operating at house load. The unit must remain running at normal frequency, feeding its own auxiliaries while completely disconnected from the grid for the 4 hours up to when resynchronisation takes place. Demonstrate that the process parameters (e.g. temperatures and vibration levels) remain stable during sustained operation at house load. |  | Open | Open | Open | Open | New Link Required
50 | Reactive Power Capability (Excitation Limiters) | Reactive Power Capability | CC.S1.1.3.3 | Yes | Demonstration of the stability of the unit at all MW/Mvar settings within the generator stability envelope at rated grid voltage. Measurement of the maximum leading/lagging reactive power capability at various loads and after thermal stabilisation of the generator. This shall also demonstrate the action of automatic limiters (OEL and UEL) to prevent the generator from operating outside its stability envelope. |  | Open | Open | N/A | Open | New Link Required
40 | Frequency Response (Governor Droop) | Operating Reserves, Governor Droop and RoCoF | CC5.3.3, CC8.8.7.3, CC8.8.7.3.3, CC.S1.1.5.5 and OC3.4.2 | Yes | Measurement of governor droop characteristic at various loads by simulation of frequency change on turbine governor. Normally measured as part of test 46 |  | Open | Open | Open | Open | New Link Required
67 | Black Start |  | CC.S1.1.4, OC7.4 and OC7.4.6.8 | Yes | Demonstrate Black Start capability |  | Open | Open | Open | Open
Key
RfG Requirements
Non-Rfg Requirements

## Phase D (hidden)
Test # | Test | Grid Code Reference | EirGrid Witness | Comment | Test procedure Agreed | Testing Completed on Primary Fuel | Testing Completed on Secondary Fuel | Test Status | Link to template procedure on website (Update all links!!)
67 | Black Start |  |  | Demonstrate Black Start capability | Open | Open | Open | Open
68 | Operating Reserves |  |  | FFR, POR, SOR, TOR1, TOR2 Tested during Operating Reserve Tests Requires data recording at 20 ms resolution for FFR Unit must assess Inertia Credit the test report. | Open | Open | Open | Open | http://www.eirgridgroup.com/site-files/library/EirGrid/Synchronous-Machine-OR-Test-Report-Template.docx
69 | Ramping Margins |  |  | Replacement Reserve Synchronised, RM1, RM3, RM8 are demonstrated during Ramp Rates test Replacement Reserve Desynchronised may be demonstrated during Hot/Warm/Cold start and ramp to full load | Open | Open | Open | Open | http://www.eirgridgroup.com/site-files/library/EirGrid/Ramping-Margin-Test-Report-Template.docx
70 | Fast Post Fault Active Power Recovery & Dynamic Reactive Response |  |  | Tested through FRT studies | Open | Open | Open | Open
71 | Steady State Reactive Power |  |  | Demonstrated during Reactive Power Capability test | Open | Open | Open | Open | http://www.eirgridgroup.com/site-files/library/EirGrid/Synchronous-SSRP-Test-Report-Template.docx
72 | Synchronous Inertial Response |  |  | Calculation based on unit Registered Characteristics | Open | Open | Open | Open | http://www.eirgridgroup.com/site-files/library/EirGrid/SSC-Synchronous-Inertial-Response.docx
Note on B2: Zia Emin: Black start test is part of RfG code if units are capable and hence moved it to FON.
Note on B3: Zia Emin: I believe these are designed as part of the DS3 regimae within EirGrid so can leave them out.