Registered Capacity Test Procedure

[Insert Unit Name]

[Insert Three Letter Code]

Version 0.1

Contents

1	DOCUMENT VERSION History	3

2	Introduction	3

3	Abbreviations	5

4	Unit DATA	5

5	soni Grid Code References	6

6	site Safety requirements	6

7	Test Description and Pre Conditions	6

7.1	Purpose	6

7.2	Pass Criteria	6

7.3	Instrumentation and Onsite Data Trending	6

7.4	Initial Conditions and Calculations	8

8	Test Steps	9

DISCLAIMER:

This Document contains information (and/or attachments) which may be privileged or confidential. All content is intended solely for the use of the individual or entity to whom it is addressed. If you are not the intended recipient please be aware that any disclosure, copying, distribution or use of the contents of this message is prohibited. If you suspect that you have received this Document in error please notify SONI or its subsidiaries immediately. SONI and its subsidiaries do not accept liability for any loss or damage arising from the use of this document or any reliance on the information it contains or the accuracy or up to date nature thereof. Use of this document and the information it contains is at the user’s sole risk. In addition, SONI and its subsidiaries strongly recommend that any party wishing to make a decision based on the content of this document should not rely solely upon data and information contained herein and should consult SONI or its subsidiaries in advance.

Further information can be found at: http://www.soni.ltd.uk/legal/

# DOCUMENT VERSION History

| Document Revision History |  |  |  |  |
| --- | --- | --- | --- | --- |
| Revision | Date | Comment | Name | Company |
| 0.1 | Xx/xx/xxxx | XX | User | User |
| 1.0 | Xx/xx/xxxx | Revised to Major version for onsite testing and signoff |  | SONI |

- Introduction

The Unit must submit the latest version of this test procedure as published on the SONI website.

Registered Capacity of a unit is an important baseline figure which is determined from this test. It is a figure expressed in nearest whole MW rounded in favour of the Generator. Should the Registered Capacity of a unit be influenced by Temperature, Humidity and Atmospheric Pressure then correction adjustments shall be made to Grid Code requirements (not IEC standards). Degrading factors of a Unit may require regular testing and adjustments of Registered Capacity. Changes to Registered capacity of a unit will subsequently trigger further testing to determine performance capabilities of a unit i.e. Block load, Ramping, Operating Reserve, Minimum Load requirements and Reactive Power Capability.

All yellow sections must be filled in before the test procedure will be approved. All grey sections must be filled in during testing. If any test requirements or steps are unclear, or if there is an issue with meeting any requirements or carrying out any steps, please contact Generator_Testing@soni.ltd.uk .

On the day of testing, suitably qualified technical personnel are required on site to assist in undertaking the tests. The personnel shall have the ability to:

- Set up and disconnect the control system and instrumentation as required;

- Ability to fully understand the Unit’s function and its relationship to the System;

- Liaise with CHCC as required;

- Mitigate issues arising during the test and report on system incidents.

The availability of personnel at CHCC will be necessary in order to initiate the necessary instructions for the test. CHCC will determine:

- If network conditions allow the testing to proceed.

- When the tests will be carried out.

On completion of this test, the following shall be submitted to Generator_Testing@soni.ltd.uk :

| Submission | Timeline |
| --- | --- |
| A scanned copy of the test procedure, as completed and signed on site on the day of testing | 1 working day |
| Test data in CSV or Excel format | 1 working day |
| Test report | 10 working days |

Note:

The NI Power System is a live, dynamic, constantly changing system on which major changes or disturbances can occur without warning. All testing has the potential to impact the NI Power System and must be treated as such.

Prior to testing taking place SONI Control Room must be informed as soon as practically possible.  SONI Control Room Staff reserve the right to suspend any testing if it may have a detrimental impact on the NI Power System and/or prevailing system conditions call for it.

Tests must be undertaken in accordance with this procedure however should a test in the procedure:

- have potential for a detrimental impact on the NI Power System,

- result in damage to the Generator’s and/or TO’s Plant and Apparatus,

- does not adequately demonstrate Generator Plant performance,

an equivalent test procedure or demonstration of Generating Unit capability agreed between SONI and the Generator may be undertaken to validate Grid Code compliance.

# Abbreviations

CHCC		Castlereagh House Control Centre

HV		High Voltage

LV		Low Voltage

MEC		Maximum Export Capacity

MVAr		Mega Volt Ampere – reactive

MW		Mega Watt

TSO		Transmission System Operator

RPM		Revolutions per minute

EDIL		Electronic Dispatch Instruction Logger

# Unit DATA

| Unit Test Coordinator | Unit to Specify Name, Company and contact details. |
| --- | --- |
| Unit name | Unit to Specify |
| Associated Station | Unit to Specify |
| Unit connection point | Unit to Specify |
| Unit connection voltage | Unit to Specify |
| Unit Fuel Type | Primary Fuel / Secondary Fuel |
| Registered Capacity | Unit to Specify |
| Contracted MEC | Unit to Specify |

Emission Limit details

| Description | Min Value | Max Value | Licence Limit |
| --- | --- | --- | --- |
| CO2 | XX mg/m3 | xxx mg/m3 | As applicable |
| O2 | XX % | xxx % | As applicable |
| CO | xxx mg/m3 | xxx mg/m3 | As applicable |
| SO2 | xxx mg/m3 | xxx mg/m3 | xxxx mg/m3 |
| NOx | xxxx mg/m3 | xxxx mg/m3 | xxxx mg/m3 |

# soni Grid Code References

| Grid Code Version: | Unit to specify |
| --- | --- |

Glossary:

| Registered Capacity | The normal Full Load capacity of a Generating Unit in MW measured as at the Connection Point and in relation to a Power Park Module, the normal Full Load capacity of the collection of one or more Generating Unit (s) taken together in aggregate, in MW measured as at the Connection Point of the Power Park Module. |
| --- | --- |

# site Safety requirements

The following is required for the SONI witness to attend site:

| Personal Protective Equipment Requirements - Site Safety boots - Hard Hat with chin strap - Hi Vis - Arc Resistive clothing - Safety Glasses - Gloves | - Yes / No - Yes / No - Yes / No - Yes / No - Yes / No - Yes / No |
| --- | --- |
| Site Induction requirements | Yes / No (If Yes, Unit to specify how and when the induction must carried out) |
| Any further information | Unit to specify |

# Test Description and Pre Conditions

## Purpose

The purpose of this test is to determine the Registered Capacity output at 0.8 power factor lagging for which the Unit can produce on a sustained basis. Sustained is the absolute minimum value achieved over the duration of the test.

## Pass Criteria

- The unit operates at its Registered Capacity and power factor of 0.8 lagging for a period of [insert no of hours as agreed with TSO but no less than 12 hours] hours.

- During operation at Registered Capacity, the unit will maintain stable operation within applicable limits.

## Instrumentation and Onsite Data Trending

All of the following trends and screenshots must be recorded by the Unit during the test. Failure to provide any of these trends will result in test cancellation.

| No. | Data Trending and Recording | Resolution | Source |
| --- | --- | --- | --- |
| 1 | Active power at Connection (MW) | Unit to specify, 100ms or as agreed with TSO | Unit to specify |
| 2 | Reactive power at Connection point (MW) | Unit to specify, 100ms or as agreed with TSO | Unit to specify |
| 3 | Active Power at Generator Terminals (MW) | Unit to specify, 100ms or as agreed with TSO | Unit to specify |
| 4 | Reactive Power at Generator Terminals (Mvar) | Unit to specify, 100ms or as agreed with TSO | Unit to specify |
| 5 | Generator Voltage (kV) | Unit to specify, 100ms or as agreed with TSO | Unit to specify |
| 6 | Turbine Speed (RPM) | Unit to specify, 100ms or as agreed with TSO | Unit to specify |
| 7 | Generator Transformer Tap setting | Unit to specify, 100ms or as agreed with TSO | Unit to specify |
| 8 | System Voltage | Unit to specify, 100ms or as agreed with TSO | Unit to specify |
| 9 | System Frequency | Unit to specify, 100ms or as agreed with TSO | Unit to specify |
| 10 | Ambient Conditions: - Temperature (ºC) - Pressure (mbar) - Humidity (%) | Unit to specify, 100ms or as agreed with TSO | Unit to specify |
| 11 | Emissions Measurements: - NOX (mg/Nm3) - SO2 (mg/Nm3) - CO2 (%) - O2 (mg/m3) - CO (mg/m3) | Unit to specify, 100ms or as agreed with TSO | Unit to specify |
| 12 | Other signals as required by the unit or by Generator_Testing@soni.ltd.uk . | Unit to specify | Unit to specify |
| 13 | Alarm/Event page | Print out alarms / events for duration of the test. |  |
| 14 | Generator Overview Screen | Print out at appropriate milestones during the test i.e. Before, during at regular intervals and after test from generator overview page on DCS |  |
| 15 | EDIL instructions | Print out as logged during the test. |  |

## Initial Conditions and Calculations

Should “No” be answered to any of the following, contact Generator_Testing@soni.ltd.uk  and agree next steps in advance of making any corrective actions.

| No. | Conditions | Check on day of test |
| --- | --- | --- |
| 1 | Test Profiles have been submitted and approved by neartime@soni.ltd.uk . | Yes/No |
| 2 | Unit Fuel Type: Primary Fuel / Secondary Fuel. | Yes/No |
| 3 | Correction curves (Temperature, humidity, atmospheric pressure) have been provided to Generator_Testing@soni.ltd.uk. | Yes/No |
| 4 | Frequency Response mode On. | Yes/No Note: If frequency response mode is Off the Unit Operator should switch it to On before continuing the test |
| 5 | Unit is on load and stable in agreement with CHCC. | Yes/No |
| 6 | Normal start up support auxiliary systems are aligned and in service. | Yes/No |
| 7 | Required signals, as described in section 7.3 are available. | Yes/No |

| No. | Calculation | Calculated on day of test |
| --- | --- | --- |
| 1 | Declared availability on day of test. | ___MW |
| 2 | Corrected Registered Capacity. | ___MW |
| 3 | Corrected Minimum load. | ___MW |

# Test Steps

| Step No. | Action | Time | Comment |
| --- | --- | --- | --- |
| 1 | Unit operator begins data recording for all trends noted in Section 7.3. |  |  |
| 2 | Unit operator contacts CHCC and requests permission to begin test and a dispatch instruction to XX MW (maximum declared availability on day of test) via EDIL. |  |  |
| 3 | Unit operator receives EDIL instruction and dispatches the Unit with a ramp rate at XX MW per minute. |  |  |
| 4 | After reaching XX MW (maximum declared availability on day of test) and following a period of XX minutes where the unit has stabilised, the Unit operator records the achieved MW value. |  | Achieved MW Output: _____MW. Corrected Registered Capacity: ___MW. |
| 5 | The Unit Operator monitors that the unit remains at XX MW for a minimum of [insert no of hours as agreed with TSO but no less than 12 hours] hours. |  | Expected time of test completion: __:__. |
| 6 | XX minutes after XX MW was achieved the Unit Operator records the minimum value sustained over this period. |  | Minimum MW value achieved over period: _____MW. Corrected Registered Capacity: ____MW. |
| 7 | XX minutes after XX MW was achieved the Unit Operator records the minimum value sustained over this period. |  | Minimum MW value achieved over period: _____MW. Corrected Registered Capacity: ____MW. |
| 8 | XX minutes after XX MW was achieved the Unit Operator records the minimum value sustained over this period. |  | Minimum MW value achieved over period: _____MW. Corrected Registered Capacity: ____MW.. |
| 9 | XX minutes after XX MW was achieved the Unit Operator records the minimum value sustained over this period. |  | Minimum MW value achieved over period: _____MW. Corrected Registered Capacity: ____MW. |
| 10 | Following XX hours, the Unit operator contacts CHCC and notifies them that the specified time period has completed. |  |  |
| 11 | Unit operator follows CHCC instruction for 30 minutes following time period at max declared availability. (Instruction may be Shutdown, Ramp up or maintain output). |  | Instruction from CHCC___________ |
| 12 | Unit operator ends data recording for all trends noted in Section 7.3. |  |  |

Comments:

Unit Witness signoff that this test has been carried out according to the test procedure above. Signature: __________________________________ Date / Time: ____________________

SONI Witness signoff that this test has been carried out according to the test procedure above. Signature: __________________________________ Date / Time: ____________________

https://www.soni.ltd.uk/how-the-grid-works/grid-codes/conventional-generator-co/index.xml

For example simulation of the Generator performance characteristics under the test procedure