## Version Control
Signal List Version Control
Version | Date | Written by: | Reviewed by: | Approved by: | Description of changes | Change requested by
Note on D3: Administrator: All signal lists circulated to EMS and ESBT for Review before issuance.

## Signal List
Providing Unit Name | Battery Signal List - System Services - FFR |  | V1.0 | 2019-01-09
Digital Output signals (from TSO) to Providing Unit |  | Permanent | 0.5 second pulse | 0.5 second pulse
|  | Common | Open | Close
Signal Description | Digital - Control | Signal | Signal | Signal
Dynamic Frequency Response Mode (Control) Enable | Control |  |  | 24V DC
Common |  | 0V DC
Dynamic Frequency Response Mode (Control) Disable | Control |  | 24V DC
Static Frequency Response Mode (Control) Enable | Control |  |  | 24V DC
Common |  | 0V DC
Static Frequency Response Mode (Control) Disable | Control |  | 24V DC
Reserve Response Mode 1 (Control) ON | Control | 0V DC | 24V DC
Reserve Response Mode 2 (Control) ON | Control | 0V DC | 24V DC
Reserve Response Mode 3 (Control) ON | Control | 0V DC | 24V DC
Reserve Response Mode 4 (Control) ON | Control | 0V DC | 24V DC
Reserve Response Mode 5 (Control) ON | Control | 0V DC | 24V DC
Digital Input Signals (to TSO) from Providing Unit |  | Permanent | 0.5 second pulse | 0.5 second pulse
|  | Common | Open | Close
Signal Description |  | Common | Signal | Signal
Dynamic Frequency Response Mode (Feedback) Enabled | Feedback |  |  | 24V DC
Common |  | 0V DC
Dynamic Frequency Response Mode (Feedback) Disabled | Feedback |  | 24V DC
Static Frequency Response Mode (Feedback) Enabled | Feedback |  |  | 24V DC
Common |  | 0V DC
Static Frequency Response Mode (Feedback) Disabled | Feedback |  | 24V DC
Reserve Response Mode 1 (Feedback) ON | Feedback |  |  | 24V DC
Common |  | 0V DC
Reserve Response Mode 1 (Feedback) OFF | Feedback |  | 24V DC
Reserve Response Mode 2 (Feedback) ON | Feedback |  |  | 24V DC
Common |  | 0V DC
Reserve Response Mode 2 (Feedback) OFF | Feedback |  | 24V DC
Reserve Response Mode 3 (Feedback) ON | Feedback |  |  | 24V DC
Common |  | 0V DC
Reserve Response Mode 3 (Feedback) OFF | Feedback |  | 24V DC
Reserve Response Mode 4 (Feedback) ON | Feedback |  |  | 24V DC
Common |  | 0V DC
Reserve Response Mode 4 (Feedback) OFF | Feedback |  | 24V DC
Reserve Response Mode 5 (Feedback) ON | Feedback |  |  | 24V DC
Common |  | 0V DC
Reserve Response Mode 5 (Feedback) OFF | Feedback |  | 24V DC

## Wiring Certificate
Providing Unit Name | Battery Signal List - System Services - FFR |  | V1.0 | 2019-01-09
Digital Output signals (from TSO) to Providing Unit |  | Permanent | 0.5 second pulse | 0.5 second pulse
|  | Common | Open | Close
Signal Description | Digital - Control | Signal | Signal | Signal | Signal in place | Functionality Confirmed
Dynamic Frequency Response Mode (Control) Enable | Control |  |  | 24V DC
Common |  | 0V DC
Dynamic Frequency Response Mode (Control) Disable | Control |  | 24V DC
Static Frequency Response Mode (Control) Enable | Control |  |  | 24V DC
Common |  | 0V DC
Static Frequency Response Mode (Control) Disable | Control |  | 24V DC
Reserve Response Mode 1 (Control) ON | Control | 0V DC | 24V DC
Reserve Response Mode 2 (Control) ON | Control | 0V DC | 24V DC
Reserve Response Mode 3 (Control) ON | Control | 0V DC | 24V DC
Reserve Response Mode 4 (Control) ON | Control | 0V DC | 24V DC
Reserve Response Mode 5 (Control) ON | Control | 0V DC | 24V DC
Digital Input Signals (to TSO) from Providing Unit |  | Permanent | 0.5 second pulse | 0.5 second pulse
|  | Common | Open | Close
Signal Description |  | Common | Signal | Signal | Signal in place | Functionality Confirmed
Dynamic Frequency Response Mode (Feedback) Enabled | Feedback |  |  | 24V DC
Common |  | 0V DC
Dynamic Frequency Response Mode (Feedback) Disabled | Feedback |  | 24V DC
Static Frequency Response Mode (Feedback) Enabled | Feedback |  |  | 24V DC
Common |  | 0V DC
Static Frequency Response Mode (Feedback) Disabled | Feedback |  | 24V DC
Reserve Response Mode 1 (Feedback) ON | Feedback |  |  | 24V DC
Common |  | 0V DC
Reserve Response Mode 1 (Feedback) OFF | Feedback |  | 24V DC
Reserve Response Mode 2 (Feedback) ON | Feedback |  |  | 24V DC
Common |  | 0V DC
Reserve Response Mode 2 (Feedback) OFF | Feedback |  | 24V DC
Reserve Response Mode 3 (Feedback) ON | Feedback |  |  | 24V DC
Common |  | 0V DC
Reserve Response Mode 3 (Feedback) OFF | Feedback |  | 24V DC
Reserve Response Mode 4 (Feedback) ON | Feedback |  |  | 24V DC
Common |  | 0V DC
Reserve Response Mode 4 (Feedback) OFF | Feedback |  | 24V DC
Reserve Response Mode 5 (Feedback) ON | Feedback |  |  | 24V DC
Common |  | 0V DC
Reserve Response Mode 5 (Feedback) OFF | Feedback |  | 24V DC
Confirmation provided by: |  | Date: