## Front Page
2022 - 2031 All Island Generation Capacity Statement Data Workbook
Purpose: To publically share the data used throughout the Generation Capacity Statement 2022-2031. For the first time, EirGrid & SONI are making the GCS report data available in a workbook format. For any questions on this data, please contact info@EirGrid.com or info@SONI.ltd.uk, referencing the GCS 2022-2031 in the subject line.
Disclaimer: EirGrid Plc and SONI Ltd have followed accepted industry practice in the collection and analysis of data available. While all reasonable care has been taken in the preparation of this data, EirGrid and SONI are not responsible for any loss that may be attributed to the use of this information. Prior to taking business decisions, interested parties are advised to seek separate and independent opinion in relation to the matters covered by this report and should not rely solely upon data and information contained herein. Information in this document does not amount to a recommendation in respect of any possible investment. This document does not purport to contain all the information that a prospective investor or participant in the Single Electricity Market (SEM) may need.
Version History:
| Version | Description | Date
| 1 | Initial Publication | 2022-10-06
| 1.01 | Ammendment made to the reported dates for ED3/5 switching to gas | 2022-10-14
Contents (In order shown in report):
| Location in Report | Description | Link
| Table 2.1 | Average annual growths for macroeconomic parameters | Demand IE
| Table 2.2 | Forecasted data centre and new tech loads demand by 2031 | Demand IE
| Figure 2.1 | Ireland demand expected from assumed build-out of data centres and new tech loads. | Demand IE
| Table 2.3 | Climate Action Plan 2021 targets for EV and Heat Pumps | Demand IE
| Figure 2.2 | EV Energy Demand – Median Scenario | Demand IE
| Figure 2.3 | Annual Heat Pump Energy Demand – Median Scenario | Demand IE
| Figure 2.4 | Total Electricity Requirement forecast for Ireland 2021 – 2031 | Demand IE
| Figure 2.5 | Ireland median demand scenario Sectoral Split | Demand IE
| Table 2.4 | Energy share per sector | Demand IE
| Figure 2.6 | Past values of recorded maximum demand in Ireland, and the ACS temperature-corrected values | Demand IE
| Figure 2.7 | The impact of Smart Metering and EV Smart Charging on the daily peak. | Demand IE
| Figure 2.8 | Impact of smartness in median scenario across the decade | Demand IE
| Figure 2.9 | Transmission peak forecast for Ireland | Demand IE
| Table 2.5 | Number of EV and Heat Pump installations included in the low, median and high demand forecast | Demand NI
| Figure 2.10 | Northern Ireland TER Forecast | Demand NI
| Figure 2.11 | Components of the TER demand forecast | Demand NI
| Figure 2.12 | ACS Transmission Peak forecasts for Northern Ireland | Demand NI
| Figure 2.13 | Combined TER forecast for the All-Island system | Demand AI
| Figure 2.14 | Transmission Peak forecast for the combined All-Island forecast. | Demand AI
| Figure 3.1 | Age breakdown of dispatchable plant on the All-Island system | Generation Availability
| Figure 3.2 | Total All-Island de-rated awarded capacity from new units in recent auctions (T-1 2022/2023, T-3 2024/2025, and T-4 2025/2026) | Generation Auction Results
| Table 3.1 | Ireland: Assumptions for new conventional plant capacities for adequacy studies (rated MW) | Generation Auction Results
| Table 3.2 | Northern Ireland Assumptions for new conventional plant capacities for adequacy studies | Generation Auction Results
| Table 3.3 | Assumptions for conventional plant changes in Ireland | Generation Conventional IE
| Table 3.4 | Assumptions for Kilroot GT plant capacity | Generation Conventional NI
| Table 3.5 | Assumptions for plant changes in Northern Ireland | Generation Conventional NI
| Table 3.6 | Capacity reliance at present on the existing North South Interconnector | Generation Non-Conventional
| Table 3.7 | Future interconnection projects | Generation Non-Conventional
| Figure 3.3 | Assumed Build-out of renewables | Generation Renewable IE
| Figure 3.4 | The actual and normalised energy produced from wind power in Ireland over the last ten years | Generation Renewable IE
| Figure 3.5 | The actual and normalised energy produced from wind power in Northern Ireland over the last ten years | Generation Renewable NI
| Figure 3.6 | Expected growth of renewable capacity installed in Northern Ireland. | Generation Renewable NI
| Table 3.8 | De-rating values used in AdCal studies | Generation Non-Conventional
| Table 3.9 | Ireland and Northern Ireland DSU Capacity (MW rated) | Generation Non-Conventional
| Table 3.10 | Total battery capacity successful in auctions (MW rated) for Ireland and Northern Ireland | Generation Non-Conventional
| Table 3.11 | Summary of availability parameters used in the T-4 2025/2026 Capacity Market auction | Generation Availability
| Figure 3.7 | The average 365-day annual system-wide availability in Ireland and Northern Ireland | Generation Availability
| Figure 3.8 | Average annual system-wide Forced Outage Rates in Ireland | Generation Availability
| Figure 3.9 | Average annual system-wide FOR in Northern Ireland | Generation Availability
| Figure 3.11 | Ireland and Northern Ireland Conventional Unit Availability | Generation Availability
| Table 4.1 | Results of adequacy studies for Ireland, given in MW of surplus plant (+) or deficit (-) | Adequacy
| Figure 4.1 | Core scenario adequacy results for Ireland, in terms of surplus or deficit of plant | Adequacy
| Table 4.2 | Loss of Load Expectation (LOLE) for Ireland in the median scenario | Adequacy
| Figure 4.2 | Adequacy results for Northern Ireland, in terms of surplus or deficit of plant (MW) | Adequacy
| Table 4.3 | Results of adequacy studies for Northern Ireland, given in MW of surplus plant (+) or deficit (-) | Adequacy
| Table 4.4 | Results of adequacy studies for Northern Ireland, given in Hrs of LOLE. | Adequacy
| Figure 4.3 | Adequacy results for the All-Island system | Adequacy
| Table 4.5 | Results of adequacy studies for the All-Island system (MW) | Adequacy
| Table 4.6 | Loss of Load Expectation (LOLE) for All-Island System (hours) | Adequacy
| Table A2-1 | Capacity Market Auction Results | Generation Auction Results
| Table A2-2 | Units issued with Termination Notices since 2021 in addition to those identified in GCS 2021 | Generation Auction Results
| Table A3-1 | Registered Capacity of dispatchable generation and interconnectors in Ireland in 2022 (MW) | Generation Conventional IE
| Table A3-2 | Partially/Non-Dispatchable plant in Ireland (MW) | Generation Renewable IE
| Table A3-3 | All Renewable energy sources in Ireland (MW). | Generation Renewable IE
| Table A3-4 | Registered Capacity of dispatchable generation and interconnectors in Northern Ireland in 2022 (MW) | Generation Conventional NI
| Table A3-5 | Partially/Non-Dispatchable plant in Northern Ireland (MW). | Generation Renewable NI
| Table A3-6 | All Renewable energy sources in Northern Ireland (MW). | Generation Renewable NI

## Demand - IE
Demand Forecast for Ireland
2.2(c) Forecasting Causal Inputs
Table 2.1 - Average annual growths for macroeconomic parameters, as advised by the ESRI
|  | 2021-2023 | 2024-2031
| Real GNI* | 6.7% | 3%
| Personal Consumption | 5.2% | 2.5%
2.2(d) Forecasting Data Centres and New Technology Loads in Ireland
Table 2.2 - Forecasted data centre and new tech loads demand by 2031, which is additional to the 600 MVA of data centre and new tech load demand assumed for 2022
| Forecast Scenario | Additional data centre/new tech load by 2031 in MVA | Overall 2031 Demand in MVA
| Low | 425 | 1025
| Median | 891 | 1491
| High | 1395 | 1995
Figure 2.1 - Ireland demand expected from assumed build-out of data centres and new tech loads. EirGrid incorporate this demand into the low, median and high demand forecast scenarios for 2031
| Year | MIC Total (MVA) | Contract Ramp (MVA) | Low Scenario (MVA) | Median Scenario (MVA) | High Scenario (MVA)
| 2016 | 462 | 360
| 2017 | 714 | 528
| 2018 | 846 | 611
| 2019 | 1036 | 698
| 2020 | 1077 | 869
| 2021 | 1752 | 1037
| 2022 | 1933 | 1371 | 695 | 752 | 830
| 2023 | 2180 | 1796 | 759 | 901 | 1078
| 2024 | 2768 | 1993 | 844 | 1044 | 1320
| 2025 | 3243 | 2083 | 887 | 1124 | 1458
| 2026 | 3243 | 2159 | 916 | 1193 | 1586
| 2027 | 3243 | 2200 | 939 | 1260 | 1707
| 2028 | 3243 | 2234 | 960 | 1325 | 1810
| 2029 | 3243 | 2270 | 982 | 1387 | 1890
| 2030 | 3243 | 2270 | 1005 | 1442 | 1954
| 2031 | 3243 | 2270 | 1025 | 1491 | 1995
2.2(e) Forecast Scenarios and Climate Action Plan 2021
Table 2.3: Climate Action Plan 2021 targets for EV and Heat Pumps
|  | EV |  |  | Heat Pump Installations
|  | Passenger | Commercial |  | Residential - New Builds | Residential - Retrofits | Commercial
| 2025 | 175000 | 20000 |  | 100000 | 100000 | 15000
| 2030 | 845000 | 95000 |  | 250000 | 400000 | 50000
Figure 2.2 – EV Energy Demand – Median Scenario
| Year | BEVs (TWh) | PHEVs (TWh) | Commercial (TWh) | Total (TWh)
| 2020 | 0.04 | 0.05 | 0.04 | 0.13
| 2021 | 0.05 | 0.05 | 0.04 | 0.14
| 2022 | 0.13 | 0.06 | 0.06 | 0.24
| 2023 | 0.21 | 0.06 | 0.07 | 0.35
| 2024 | 0.29 | 0.07 | 0.09 | 0.45
| 2025 | 0.37 | 0.07 | 0.11 | 0.55
| 2026 | 0.6 | 0.12 | 0.18 | 0.89
| 2027 | 0.82 | 0.16 | 0.25 | 1.24
| 2028 | 1.05 | 0.21 | 0.32 | 1.58
| 2029 | 1.27 | 0.25 | 0.4 | 1.92
| 2030 | 1.5 | 0.3 | 0.47 | 2.27
| 2031 | 1.65 | 0.33 | 0.51 | 2.49
Figure 2.3 – Annual heat Pump Energy Demand
| Year | New Builds - Residential (TWh) | Retrofits - Residential (TWh) | Commercial (TWh) | Total (TWh)
| 2020 | 0.2 | 0.1 | 0.1 | 0.3
| 2021 | 0.2 | 0.2 | 0.1 | 0.5
| 2022 | 0.3 | 0.2 | 0.1 | 0.6
| 2023 | 0.3 | 0.3 | 0.1 | 0.7
| 2024 | 0.3 | 0.4 | 0.1 | 0.8
| 2025 | 0.3 | 0.5 | 0.2 | 1
| 2026 | 0.4 | 0.7 | 0.2 | 1.4
| 2027 | 0.5 | 1 | 0.3 | 1.8
| 2028 | 0.6 | 1.2 | 0.4 | 2.2
| 2029 | 0.7 | 1.5 | 0.5 | 2.7
| 2030 | 0.8 | 1.7 | 0.5 | 3.1
| 2031 | 0.9 | 1.9 | 0.6 | 3.4
2.2(f) Total Electricity Requirement (TER)
Figure 2.4 - Total Electricity Requirement forecast for Ireland 2021 – 2031
|  | Historical (TWh) | GCS21 (TWh) |  |  | GCS22 (TWh)
| Year |  | Low | Median | High | Low | Median | High
| 2018 | 29.8
| 2019 | 30.4
| 2020 | 30.5
| 2021 | 31.7 | 31.6 | 32.1 | 32.6
| 2022 |  | 32.2 | 33.3 | 34.5 | 33 | 33.7 | 34.4
| 2023 |  | 33.4 | 34.7 | 36.6 | 34.1 | 35.7 | 37.2
| 2024 |  | 34.1 | 35.8 | 38.4 | 35.4 | 37.5 | 40.1
| 2025 |  | 34.5 | 36.5 | 39.6 | 36 | 38.5 | 41.6
| 2026 |  | 35 | 37.5 | 41 | 37 | 39.9 | 43.6
| 2027 |  | 35.6 | 38.4 | 42.5 | 37.8 | 41.3 | 45.6
| 2028 |  | 36.2 | 39.4 | 44.1 | 38.6 | 42.7 | 47.4
| 2029 |  | 36.6 | 40.1 | 45.3 | 39.3 | 43.9 | 48.8
| 2030 |  | 37.1 | 40.9 | 46.5 | 40 | 45.1 | 50.1
| 2031 |  |  |  |  | 40.6 | 46.1 | 51.2
Figure 2.5 - For the Ireland median demand scenario, this illustrates the approximate split into different sectors. EirGrid estimate that 28% of total demand will come from data centres and new tech loads by 2031
| Year | Residential (excl. EV&HP) (TWh) | Commercial (TWh) | Industrial (excl. Data Centres & New Tech Loads) (TWh) | Data Centres and New Tech Loads (TWh) | EVs and Heat Pumps (TWh)
| 2016 | 9 | 8 | 9.5 | 1.7 | 0
| 2017 | 9.1 | 8.4 | 9.3 | 2.3 | 0
| 2018 | 9.3 | 8.6 | 8.6 | 3.2 | 0
| 2019 | 9.3 | 8.6 | 8.6 | 3.8 | 0.2
| 2020 | 9.3 | 7.6 | 8.6 | 4.6 | 0.5
| 2021 | 9.5 | 7.7 | 8.6 | 5.3 | 0.6
| 2022 | 9.8 | 7.9 | 8.6 | 6.6 | 0.8
| 2023 | 10.1 | 8 | 8.6 | 7.9 | 1.1
| 2024 | 10.3 | 8.2 | 8.6 | 9.1 | 1.3
| 2025 | 10.4 | 8.2 | 8.6 | 9.8 | 1.5
| 2026 | 10.4 | 8.2 | 8.6 | 10.4 | 2.3
| 2027 | 10.4 | 8.2 | 8.6 | 11 | 3
| 2028 | 10.3 | 8.3 | 8.6 | 11.6 | 3.8
| 2029 | 10.2 | 8.3 | 8.6 | 12.1 | 4.6
| 2030 | 10.1 | 8.4 | 8.6 | 12.6 | 5.4
| 2031 | 10.1 | 8.4 | 8.6 | 13.1 | 5.9
Table 2.4 - Energy share per sector
|  | 2021 (%) | 2031 (%)
| Residential (excl. EV/HP) | 30 | 22
| Commercial | 24 | 18
| Industry (excl. DC + new tech loads) | 27 | 19
| DC + new tech loads | 17 | 28
| EV + Heat Pumps | 2 | 13
2.2(g) Peak Demand Forecasting – Temperature Correction
Figure 2.6 - Past values of recorded maximum demand in Ireland, and the ACS temperature-corrected values
| Year | Network Exported Peak (TW) | Historic Temperature-Corrected Peak (TW)
| 2002/03 | 4.25 | 4.33
| 2003/04 | 4.18 | 4.27
| 2004/05 | 4.38 | 4.56
| 2005/06 | 4.67 | 4.85
| 2006/07 | 4.86 | 5.02
| 2007/08 | 4.91 | 5.11
| 2008/09 | 4.89 | 4.9
| 2009/10 | 4.99 | 4.87
| 2010/11 | 5.09 | 4.9
| 2011/12 | 4.64 | 4.82
| 2012/13 | 4.59 | 4.73
| 2013/14 | 4.52 | 4.8
| 2014/15 | 4.7 | 4.89
| 2015/16 | 4.67 | 4.97
| 2016/17 | 4.75 | 4.97
| 2017/18 | 4.94 | 5.05
| 2018/19 | 4.91 | 5.18
| 2019/20 | 5.01 | 5.15
| 2020/21 | 5.35 | 5.37
| 2021/22 | 5.35 | 5.53
2.2(h) Peak Demand Forecasting – Impact of ‘Smartness’
Figure 2.7 – The impact of Smart Metering and EV Smart Charging on the daily peak. The above graph is indicative of the peak day in the 2030 median scenario
| Hr | with Smart Metering & Smart EV Charging (MW) | with Smart Meter (MW) | No 'Smartness' (MW)
| 0 | 5730 | 5730 | 5520
| 1 | 5590 | 5590 | 5290
| 2 | 5500 | 5500 | 5130
| 3 | 5460 | 5460 | 5060
| 4 | 5430 | 5430 | 5060
| 5 | 5500 | 5500 | 5220
| 6 | 5780 | 5780 | 5620
| 7 | 6250 | 6250 | 6210
| 8 | 6460 | 6460 | 6570
| 9 | 6550 | 6550 | 6680
| 10 | 6570 | 6570 | 6670
| 11 | 6590 | 6590 | 6680
| 12 | 6620 | 6620 | 6700
| 13 | 6580 | 6580 | 6680
| 14 | 6610 | 6610 | 6690
| 15 | 6690 | 6950 | 7050
| 16 | 6880 | 7140 | 7300
| 17 | 6980 | 7240 | 7500
| 18 | 6890 | 7150 | 7480
| 19 | 6720 | 6980 | 7260
| 20 | 6570 | 6570 | 6780
| 21 | 6370 | 6370 | 6500
| 22 | 6080 | 6080 | 6120
| 23 | 5900 | 5900 | 5820
Figure 2.8 - Impact of Smartness in median Scenario across the decade
| Year | with Smart Metering + Smart EV Charging (MW) | with Smart Metering (MW) | No 'Smartness' (MW)
| 2021 | 5550 | 5580 | 5600
| 2022 | 5750 | 5800 | 5840
| 2023 | 6010 | 6090 | 6140
| 2024 | 6250 | 6350 | 6420
| 2025 | 6360 | 6490 | 6570
| 2026 | 6450 | 6610 | 6740
| 2027 | 6570 | 6750 | 6930
| 2028 | 6680 | 6890 | 7120
| 2029 | 6780 | 7010 | 7300
| 2030 | 6870 | 7130 | 7460
| 2031 | 6940 | 7230 | 7600
2.2(i) Peak Demand Forecasting – Overall
Figure 2.9 - Transmission peak forecast for Ireland
|  | Historical (GW) | GCS21 (GW) |  |  | GCS22 (GW)
| Year |  | Low | Median | High | Low | Median | High
| 2016 | 5
| 2017 | 5.1
| 2018 | 5.2
| 2019 | 5.2
| 2020 | 5.4
| 2021 | 5.5 | 5.4 | 5.5 | 5.7
| 2022 |  | 5.5 | 5.7 | 5.8 | 5.6 | 5.7 | 5.9
| 2023 |  | 5.5 | 5.9 | 6.1 | 5.7 | 6 | 6.2
| 2024 |  | 5.5 | 6 | 6.3 | 5.8 | 6.3 | 6.5
| 2025 |  | 5.6 | 6.1 | 6.4 | 5.8 | 6.4 | 6.7
| 2026 |  | 5.6 | 6.1 | 6.5 | 5.8 | 6.5 | 6.9
| 2027 |  | 5.6 | 6.2 | 6.7 | 5.9 | 6.6 | 7
| 2028 |  | 5.6 | 6.3 | 6.8 | 5.9 | 6.7 | 7.2
| 2029 |  | 5.7 | 6.4 | 6.9 | 5.9 | 6.8 | 7.3
| 2030 |  | 5.7 | 6.5 | 7 | 5.9 | 6.9 | 7.4
| 2031 |  |  |  |  | 6 | 6.9 | 7.5
Data Centre Demand
|  | Historical (MW) | GCS22 (MW)
| Year |  | Low | Median | High
| 2016 | 134
| 2017 | 174
| 2018 | 256
| 2019 | 319
| 2020 | 410
| 2021 | 490
| 2022 |  | 544 | 591 | 652
| 2023 |  | 601 | 695 | 840
| 2024 |  | 659 | 784 | 1010
| 2025 |  | 702 | 864 | 1148
| 2026 |  | 731 | 933 | 1276
| 2027 |  | 754 | 1000 | 1397
| 2028 |  | 775 | 1065 | 1500
| 2029 |  | 797 | 1127 | 1580
| 2030 |  | 820 | 1182 | 1644
| 2031 |  | 840 | 1231 | 1685
*Note, for the purposes of forecasting, the GCS assumes unity power factor (1 MVA = 1 MW)

## Demand - NI
Demand Forecast for Northern Ireland
2.3(b) Demand Scenarios
Table 2.5 - Number of EV and Heat Pump installations included in the median demand forecast
|  | Low |  | Median |  | High
|  | Electric Vehicles | Heat Pump Installations | Electric Vehicles | Heat Pump Installations | Electric Vehicles | Heat Pump Installations
| 2025 | 35000 | 16000 | 64000 | 42000 | 86000 | 42000
| 2030 | 158000 | 26000 | 273000 | 67000 | 372000 | 67000
2.3(d) TER Forecast
Figure 2.10 - Northern Ireland TER Forecast
| Year | Historical (TWh) | GCS21 Median (TWh) | GCS22 Low (TWh) | GCS22 Median (TWh) | GCS22 High (TWh)
| 2016 | 9
| 2017 | 8.8
| 2018 | 9
| 2019 | 8.7
| 2020 | 8.3
| 2021 | 8.6 | 8.4
| 2022 |  | 8.5 | 8.5 | 8.8 | 9
| 2023 |  | 8.5 | 8.5 | 8.9 | 9.4
| 2024 |  | 8.6 | 8.5 | 9.1 | 9.8
| 2025 |  | 8.6 | 8.5 | 9.3 | 10.2
| 2026 |  | 8.6 | 8.5 | 9.6 | 10.8
| 2027 |  | 8.6 | 8.5 | 9.7 | 11
| 2028 |  | 8.7 | 8.6 | 9.9 | 11.3
| 2029 |  | 8.7 | 8.6 | 10 | 11.6
| 2030 |  | 8.7 | 8.6 | 10.2 | 12
| 2031 |  |  | 8.6 | 10.4 | 12.4
Figure 2.11 - Illustrates how the TER demand forecast is built up from the various demand components for the years 2025 and 2030. Growth in TER from 2025 is primarily driven by the electrification of heat and transport with government policies and incentives expected to drive growth.
|  | Transport | Residential | Industrial | Tertiary | Losses | Total
| 2025 | 0.24 | 2.79 | 3.35 | 1.9 | 1 | 9.28
| 2030 | 0.75 | 2.86 | 3.63 | 1.87 | 1.07 | 10.18
2.3(e) Peak Demand Forecasting
Figure 2.12 - ACS Transmission Peak forecasts for Northern Ireland
| Year | Historical (GW) | GCS21 Median (GW) | GCS22 Low (GW) | GCS22 Median (GW) | GCS22 High (GW)
| 2011 | 1.71
| 2012 | 1.75
| 2013 | 1.72
| 2014 | 1.69
| 2015 | 1.72
| 2016 | 1.72
| 2017 | 1.69
| 2018 | 1.68
| 2019 | 1.71
| 2020 | 1.63
| 2021 | 1.62 | 1.65
| 2022 |  | 1.65 | 1.56 | 1.64 | 1.76
| 2023 |  | 1.66 | 1.56 | 1.66 | 1.78
| 2024 |  | 1.67 | 1.56 | 1.68 | 1.8
| 2025 |  | 1.68 | 1.56 | 1.7 | 1.86
| 2026 |  | 1.69 | 1.57 | 1.75 | 1.93
| 2027 |  | 1.7 | 1.57 | 1.77 | 1.98
| 2028 |  | 1.71 | 1.57 | 1.79 | 2.02
| 2029 |  | 1.71 | 1.58 | 1.81 | 2.07
| 2030 |  | 1.71 | 1.58 | 1.83 | 2.12
| 2031 |  |  | 1.59 | 1.86 | 2.17

## Demand - AI
Demand Forecast for All-Island
2.4 The Combined All-Island Forecast
Figure 2.13 - Combined TER forecast for the All-Island system.
| Year | Historical (TWh) | GCS21 Median (TWh) | GCS22 Low (TWh) | GCS22 Median (TWh) | GCS22 High (TWh)
| 2018 | 38.8
| 2019 | 39.1
| 2020 | 38.9
| 2021 | 40.3 | 40.5
| 2022 |  | 41.8 | 41.5 | 42.5 | 43.4
| 2023 |  | 43.2 | 42.6 | 44.6 | 46.6
| 2024 |  | 44.3 | 44 | 46.6 | 49.9
| 2025 |  | 45 | 44.6 | 47.8 | 51.8
| 2026 |  | 46.1 | 45.5 | 49.5 | 54.4
| 2027 |  | 47 | 46.3 | 51 | 56.6
| 2028 |  | 48 | 47.2 | 52.6 | 58.8
| 2029 |  | 48.8 | 47.8 | 53.9 | 60.4
| 2030 |  | 49.6 | 48.5 | 55.2 | 62.1
| 2031 |  |  | 49.2 | 56.5 | 63.5
Figure 2.14 - Transmission Peak forecast for the combined All-Island forecast.
| Year | Historical (GW) | GCS21 Median (GW) | GCS22 Low (GW) | GCS22 Median (GW) | GCS22 High (GW)
| 2018 | 6.78
| 2019 | 6.9
| 2020 | 6.98
| 2021 | 7.12 | 7.14
| 2022 |  | 7.33 | 7.11 | 7.34 | 7.63
| 2023 |  | 7.45 | 7.21 | 7.62 | 7.94
| 2024 |  | 7.57 | 7.31 | 7.9 | 8.31
| 2025 |  | 7.67 | 7.34 | 8.07 | 8.54
| 2026 |  | 7.77 | 7.35 | 8.16 | 8.76
| 2027 |  | 7.87 | 7.4 | 8.3 | 8.98
| 2028 |  | 7.97 | 7.43 | 8.43 | 9.18
| 2029 |  | 8.06 | 7.46 | 8.56 | 9.35
| 2030 |  | 8.15 | 7.49 | 8.67 | 9.5
| 2031 |  |  | 7.5 | 8.77 | 9.63

## Generation - Conventional IE
Conventional Generation - IE
3.2 Changes to Conventional Generation in Ireland
Table 3.3 -Assumptions for conventional plant changes in Ireland
| Plant | Units | Export Capacity (MW) | Modelled as closing by the end of: | Comment
| Aghada | AT1 | 90 | 2023 | IED Limited Life-time Derogation. ESB has provided a closure notice for these units.
|  | AD2 | 449 | Remains open for study horizon | Note AD2 has increased capacity from 431 MW to 449 MW
| Tarbert | TB1 | 54 | 2021 | SSE has previously provided a closure notice for this unit to close at end of 2023. TB1 has since been placed on outage until Dec 2023 so will be excluded from studies
|  | TB2 | 54 | 2021 | SSE has previously provided a closure notice for this unit to close at end of 2023. TB2 has since been placed on outage until Dec 2023 so will be excluded from studies
|  | TB3 | 241 | 2023 | SSE has provided a closure notice for this unit to close at end of 2023.
|  | TB4 | 243 | 2021 | SSE has previously provided a closure notice for this unit to close at end of 2023. TB4 has since been placed on outage until end of March 2023. Will be excluded from studies
| Moneypoint | MP1 | 285 | 2024 | Moneypoint units could not qualify for the 2024/2025 T-4 Capacity Auction[1]. On this basis, these units will be excluded from end of 2024. EirGrid notes that ESB has not provided a closure notice for these units. MP2 is now running on HFO with a capacity of 250 MW.
|  | MP2 | 250
|  | MP3 | 285
| Edenderry | ED1 | 118 | 2030 | The Bord na Móna plant ED1 was due to close at the end of 2023. Planning permission was recently awarded to keep this unit operating until 2030, running on 100% biomass from 2024.
Appendix 3 Generation Plant Information
Table A3-1 Registered Capacity of dispatchable generation and interconnectors in Ireland in 2022 (MW) DSU: Demand Side Unit; HFO: Heavy Fuel Oil; DO: Distillate Oil
|  | ID | Fuel Type | Technology Category | 2022 | Comment
| Aghada | AT1 | Gas/DO | Gas Turbine | 90 | To close before end of 2023
|  | AT2 | Gas/DO | Gas Turbine | 90
|  | AT4 | Gas/DO | Gas Turbine | 90
|  | AD2 | Gas/DO | Gas Turbine | 449 | Increased capacity from 431 MW
| All DSU | DSU | DSU | DSU | 604
| Ardnacrusha | AA1-4 | Hydro | Hydro | 86
| Dublin Bay | DB1 | Gas/DO | Gas Turbine | 415
| Dublin Waste | DW1 | Waste | Steam Turbine | 61
| Edenderry | ED1 | Milled peat/ Biomass | Steam Turbine | 118 | Planning Permission was granted to extend operation to 2030. Will run exclusively on biomass from Jan 2024
|  | ED3 | DO/Gas | Gas Turbine | 58 | Operating on gas from Oct 2025
|  | ED5 | DO/Gas | Gas Turbine | 58 | Operating on gas from Oct 2025
| Erne | ER1-4 | Hydro | Hydro | 65
| EWIC | EW1 | DC Interconnector |  | 500
| Great Island CCGT | GI4 | Gas/DO | Gas Turbine | 464
| Huntstown | HNC | Gas/DO | Gas Turbine | 337
|  | HN2 | Gas/DO | Gas Turbine | 408
| Indaver Waste | IW1 | Waste | Steam Turbine | 17
| Lee | LE1-4 | Hydro | Hydro | 27
| Liffey | LI1-4 | Hydro | Hydro | 38
| Moneypoint | MP1 | Coal/HFO | Steam Turbine | 285 | Modelled as not available from October 2024
|  | MP2 | HFO | Steam Turbine | 250 | Modelled as not available from October 2024
|  | MP3 | Coal/HFO | Steam Turbine | 285 | Modelled as not available from October 2024
| Poolbeg CC | PBA | Gas/DO | Gas Turbine | 234
|  | PBB | Gas/DO | Gas Turbine | 234
| Rhode | RP1 | DO | Gas Turbine | 52
|  | RP2 | DO | Gas Turbine | 52
| Sealrock | SK3 | Gas/DO | Gas Turbine | 81
|  | SK4 | Gas/DO | Gas Turbine | 81
| Tarbert | TB1 | HFO | Steam Turbine | 54 | Unit has been placed on outage until Dec 2023. Scheduled to close thereafter
|  | TB2 | HFO | Steam Turbine | 54 | Unit has been placed on outage until Dec 2023. Scheduled to close thereafter
|  | TB3 | HFO | Steam Turbine | 241 | To close by end of 2023
|  | TB4 | HFO | Steam Turbine | 243 | Unit has been placed on outage until March 2023. Scheduled to close by end 2023
| Tawnaghmore | TP1 | DO | Gas Turbine | 52
|  | TP3 | DO | Gas Turbine | 52
| Turlough Hill | TH1 | Pumped storage | Storage | 292
| Tynagh | TYC | Gas/DO | Gas Turbine | 389
| Whitegate | WG1 | Gas/DO | Gas Turbine | 450
| Total Dispatchable including DSU |  |  |  | 7356

## Generation - Conventional NI
Conventional Generation - NI
3.3 Changes to Conventional Generation in Northern Ireland
Table 3.4 - Assumptions for Kilroot GT plant capacity
| Plant | Export Capacity (MW) | Modelling Assumption | Comment
| KGT1 | 29 | Unavailable in 2025 | Did not qualify for inclusion in T-4 2024/25 auction
| KGT2 | 29 | Unavailable in 2025 | Did not qualify for inclusion in T-4 2024/25 auction
| KGT3 | 42 | Unavailable in 2025 | Did not qualify for inclusion in T-4 2024/25 auction
| KGT4 | 42 | Unavailable in 2025 | Did not qualify for inclusion in T-4 2024/25 auction
Table 3.5 - Assumptions for plant changes in Northern Ireland
| Plant | Export Capacity (MW) | Modelled as closing by the end of: | Comment
| Kilroot ST1 | 238 | 2023 | EPUKI has provided a closure notice for this unit. Operation ceases 30th September 2023. The 238 MW is based on the HFO rating, however the station has been declared unavailable for HFO operation for significant periods during 2021. Due to Environmental Permit Compliance Restrictions, the unit is assumed to be 130 MW for modelling purposes.
| Kilroot ST2 | 238 | 2023 | EPUKI has provided a closure notice for this unit. Operation ceases 30th September 2023. The 238 MW is based on the HFO rating, however the station has been declared unavailable for HFO operation for significant periods during 2021. Due to Environmental Permit Compliance Restrictions, the unit is assumed to be 130 MW for modelling purposes.
Appendix 3 Generation Plant Information
Table A3-4 Registered Capacity of dispatchable generation and interconnectors in Northern Ireland in 2022 (MW).
|  | ID | Fuel Type | Technology Category | 2022 | Comment
| Ballylumford | B31 | Gas/Heavy Fuel Oil | Gas Turbine | 246
|  | B32 | Gas/Heavy Fuel Oil | Gas Turbine | 246
|  | B10 | Gas/Heavy Fuel Oil | Gas Turbine | 101
|  | GT7(GT1) | Distillate Oil | Gas Turbine | 58
|  | GT8(GT2) | Distillate Oil | Gas Turbine | 58
| Kilroot | ST1 | Heavy Fuel Oil/Coal | Steam Turbine | 238 | Ceases operation in 2023
|  | ST2 | Heavy Fuel Oil/Coal | Steam Turbine | 238 | Ceases operation in 2023
|  | KGT1 | Distillate Oil | Gas Turbine | 29
|  | KGT2 | Distillate Oil | Gas Turbine | 29
|  | KGT3 | Distillate Oil | Gas Turbine | 42
|  | KGT4 | Distillate Oil | Gas Turbine | 42
| Coolkeeragh | GT8 | Distillate Oil | Gas Turbine | 53
|  | C30 | Gas/Distillate Oil | Gas Turbine | 408
| AGU | AGU | Distillate Oil | Gas Turbine | 79
| DSU | DSU | Various | DSU | 143
| Lisahally |  | Biomass |  | 18 | Not in Capacity Market, but assumed available for capacity requirement
| Contour Global | CGA / CGC | Gas | Gas Turbine | 12
| Moyle |  | DC Interconnector |  | 450
| Total Dispatchable plant: |  |  |  | 2490

## Generation - Renewable IE
Renewable Generation - IE
3.5(a) Wind Power in Ireland
Figure 3.3 - Assumed Build-out of renewables
| Year | Waste (GW) | Biomass (GW) | Solar (GW) | Onshore Wind (GW) | Offshore Wind (GW) | Hydro (GW)
| 2019 | 0.077 | 0.088 | 0.016 | 4.088 | 0.025 | 0.242
| 2020 | 0.077 | 0.088 | 0.139 | 4.234 | 0.025 | 0.242
| 2021 | 0.077 | 0.088 | 0 | 4.33 | 0.025 | 0.242
| 2022 | 0.077 | 0.131 | 0.167 | 4.482 | 0.025 | 0.242
| 2023 | 0.077 | 0.131 | 0.333 | 4.634 | 0.025 | 0.242
| 2024 | 0.077 | 0.172 | 0.5 | 4.787 | 0.025 | 0.242
| 2025 | 0.077 | 0.172 | 0.667 | 4.939 | 0.025 | 0.242
| 2026 | 0.077 | 0.172 | 0.833 | 5.091 | 0.025 | 0.242
| 2027 | 0.077 | 0.172 | 1 | 5.243 | 0.025 | 0.242
| 2028 | 0.077 | 0.172 | 1.167 | 5.396 | 0.725 | 0.242
| 2029 | 0.077 | 0.172 | 1.333 | 5.548 | 2.863 | 0.242
| 2030 | 0.077 | 0.172 | 1.5 | 5.7 | 5 | 0.242
| 2031 | 0.077 | 0.172 | 1.667 | 5.852 | 7.138 | 0.242
Figure 3.4 - The actual and normalised energy produced from wind power in Ireland over the last ten years
| Year | Wind Installed Capacity (MW) | Total Wind Generation (GWh) | Normalised Wind Generation (GWh) | Wind CapacityFactor | Average Capacity Factor
| 2012 | 1700 | 4100 | 4120 | 28% | 28%
| 2013 | 1920 | 4640 | 4600 | 29%
| 2014 | 2270 | 5120 | 5250 | 28%
| 2015 | 2450 | 6540 | 6190 | 32%
| 2016 | 2800 | 6120 | 6600 | 27%
| 2017 | 3310 | 7230 | 7580 | 27%
| 2018 | 3670 | 8690 | 8630 | 28%
| 2019 | 4120 | 9530 | 9620 | 28%
| 2020 | 4300 | 11140 | 10410 | 30%
| 2021 | 4330 | 9530 | 10500 | 25%
Appendix 3 Generation Plant Information
Table A3-2 Partially/Non-Dispatchable plant in Ireland (MW)
| At year end: | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| Wind Onshore* | 4480 | 4630 | 4790 | 4940 | 5100 | 5250 | 5400 | 5550 | 5700 | 5850
| Wind Offshore* | 25 | 25 | 25 | 25 | 25 | 25 | 725 | 2865 | 5000 | 7140
| Small Scale Hydro | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
| Biomass and Biogas | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| Biomass CHP | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
| Industrial | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
| Conventional CHP | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129
| Solar PV | 167 | 333 | 500 | 667 | 833 | 1000 | 1167 | 1333 | 1500 | 1667
| Total | 4890 | 5206 | 5533 | 5850 | 6176 | 6493 | 7510 | 9966 | 12418 | 14875
Table A3-3 All Renewable energy sources in Ireland (MW). We have assumed that the peat plant at Edenderry will be approximately 60% powered by biomass by 2021 and 100% biomass from 2024 onwards
| At year end: | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| All Wind* | 4505 | 4655 | 4815 | 4965 | 5125 | 5275 | 6125 | 8415 | 10700 | 12990
| All Hydro | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242
| Biomass/LFG (including those units registered in the Capacity Market and Biomass CHP) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| Waste (Assume 50% renewable) | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
| Peat Stations on Biomass | 77 | 77 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 0
| Solar | 167 | 333 | 500 | 667 | 833 | 1000 | 1167 | 1333 | 1500 | 1667
| Total RES | 5054 | 5370 | 5738 | 6055 | 6381 | 6698 | 7715 | 10171 | 12623 | 14962

## Generation - Renewable NI
Renewable Generation - NI
3.5(b) Wind Power in Northern Ireland
Figure 3.5- The actual and normalised energy produced from wind power in Northern Ireland over the last ten years
| Year | Wind Installed Capacity (MW) | Total Wind Generation (GWh) | Normalised Wind Generation (GWh) | Wind CapacityFactor (%) | Average Capacity Factor (%)
| 2012 | 600 | 1020 | 1120 | 21% | 23%
| 2013 | 640 | 1260 | 1250 | 23%
| 2014 | 730 | 1450 | 1360 | 24%
| 2015 | 750 | 1800 | 1570 | 28%
| 2016 | 940 | 1730 | 1780 | 23%
| 2017 | 1150 | 2050 | 2210 | 22%
| 2018 | 1280 | 2390 | 2520 | 22%
| 2019 | 1280 | 2460 | 2600 | 22%
| 2020 | 1280 | 2630 | 2540 | 24%
| 2021 | 1350 | 2170 | 2510 | 19%
Figure 3.6- Growth of renewable capacity installed in Northern Ireland.
| Year | Waste (GW) | Biomass (GW) | Solar (GW) | Onshore Wind (GW) | Offshore Wind (GW) | Hydro (GW)
| 2022 | 0.015 | 0.079 | 0.285 | 1.43 | 0 | 0.006
| 2023 | 0.015 | 0.079 | 0.285 | 1.56 | 0 | 0.006
| 2024 | 0.015 | 0.079 | 0.285 | 1.68 | 0 | 0.006
| 2025 | 0.015 | 0.079 | 0.335 | 1.81 | 0 | 0.006
| 2026 | 0.015 | 0.079 | 0.395 | 1.94 | 0 | 0.006
| 2027 | 0.015 | 0.079 | 0.455 | 2.07 | 0 | 0.006
| 2028 | 0.015 | 0.079 | 0.505 | 2.2 | 0 | 0.006
| 2029 | 0.015 | 0.079 | 0.565 | 2.33 | 0 | 0.006
| 2030 | 0.015 | 0.079 | 0.615 | 2.55 | 0.1 | 0.006
| 2031 | 0.015 | 0.079 | 0.675 | 2.58 | 0.1 | 0.006
Appendix 3 Generation Plant Information
Table A3-5 Partially/Non-Dispatchable plant in Northern Ireland (MW).
| At year end: | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| Large Scale Wind* | 1250 | 1380 | 1500 | 1630 | 1760 | 1890 | 2020 | 2150 | 2370 | 2500
| Small Scale Wind | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
| Solar PV | 285 | 285 | 285 | 335 | 395 | 455 | 505 | 565 | 615 | 675
| Small Scale Biogas | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| Landfill Gas | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
| Small Scale Biomass | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Renewable CHP | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Other CHP | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Small Scale Hydro | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Waste-to-Energy | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
| Total | 1791 | 1921 | 2041 | 2221 | 2411 | 2601 | 2781 | 2971 | 3241 | 3431
Table A3-6 All Renewable energy sources in Northern Ireland (MW).
| At year end: | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| All Wind* | 1430 | 1560 | 1680 | 1810 | 1940 | 2070 | 2200 | 2330 | 2550 | 2680
| Solar PV | 285 | 285 | 285 | 335 | 395 | 455 | 505 | 565 | 615 | 675
| All Biomass/Biogas/LFGas/WTE | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
| Renewable CHP | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Hydro | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Total RES | 1803 | 1933 | 2053 | 2233 | 2423 | 2613 | 2793 | 2983 | 3253 | 3443

## Generation - Auction Results
Generation Auction Results
3.1(a) SEM Capacity Market Auction Results
Figure 3.2 - Total All-Island de-rated awarded capacity from recent auctions (T-1 2022/2023, T-3 2024/2025, and T-4 2025/2026)
| Auction | Gas Turbine (MWd) | Battery (MWd) | DSU (MWd)
| T-1 22/23 | 5 | 53 | 40
| T-3 24/25 | 1165 | 144 | 42
| T-4 25/26 | 521 | 103 | 64
Table 3.1– Ireland: Assumptions for new conventional plant capacities for adequacy studies (rated MW) from T-1 22/23, T-4 24/25, T-3 24/25 and T-4 25/26. Note values are rounded to nearest 10.
| Ireland | 2023 | 2024 | 2025 | 2026 | 2027
| Gas Turbine | 0 | 120 | 190 | 790* | 140
* Denotes that there are units within this calendar year that are subject to ARHL
Table 3.2- Northern Ireland Assumptions for new conventional plant capacities for adequacy studies, including ARHL factor (rated MW) from T-1 22/23, T-4 24/25, T-3 24/25 and T-4 25/26. Note values are rounded to nearest 10.
| Northern Ireland | 2023 | 2024 | 2025 | 2026 | 2027
| Gas Turbine | 0 | 720 | 0 | 0** | 0
| Steam Turbine | 0 | 0 | 0 | 310 | 0
** ARHL removed as station converts to CCGT. This will increase the overall contribution to system adequacy
Appendix 2– Auction Results
Table A2-1 Capacity Market Auction Results
| Auction | Date | Awarded Capacity (De-Rated)
| 2018/2019 T-1 | 2017-12-15 | 7.774 GW
| 2019/2020 T-1 | 2018-12-13 | 8.266 GW
| 2020/2021 T-1 | 2019-11-26 | 7.606 GW
| 2021/2022 T-2 | 2019-12-05 | 7.512 GW
| 2022/2023 T-4 | 2019-03-28 | 7.412 GW
| 2023/2024 T-4 | 2020-04-27 | 7.322 GW
| 2024/2025 T-4 | 2021-01-21 | 6.168 GW
| 2022/2023 T-1 | 2021-10-21 | 1.121 GW
| 2024/2025 T-3 | 2022-01-20 | 1.471 GW
| 2025/2026 T-4 | 2022-03-24 | 6.484 GW
Table A2-2 - Units issued with Termination Notices since 2021 in addition to those identified in GCS 2021
| Plant | Technology Type | SEM CRM Auction | Awarded New Capacity Terminated (MW) | Termination issued
| ESB-FlexGen | Gas Turbine | T-4 22/23 | 192.36 | 2021
| EnerNoc | DSU | T-4 22/23 | 60.7 | 2021
| ESB | Gas Turbine | T-4 23/24 | 11.49 | 2021
| ESB | Gas Turbine | T-4 24/25 | 10.14 | 2021
| EnerNoc | DSU | T-2 21/22 | 2.64 | 2021
| Statkraft | Gas Turbine | T-4 24/25 | 45.1 | 2021
| EnerNoc | DSU | T-2 21/22 | 1.51 | 2021
| Energia | Gas Turbine | T-4 23/24 | 17.64 | 2022
| EnerNOC | DSU | T-4 23/24 | 12.15 | 2022
| Rhode Energy Storage | Battery | T-4 24/25 | 14.25 | 2022
|  | Total |  | 367.98

## Generation - Non-Conventional
Non-Conventional Generation
3.4(a) North South Interconnector
Table 3.6 - Capacity reliance at present on the existing North South Interconnector
|  | North to South | South to North
| Capacity Reliance | 100 MW | 200 MW
3.4(c) Further Interconnection
Table 3.7- Future interconnection projects
| Project | Description | Project Promoters Target Commissioning Year
| Celtic Interconnector | Interconnector between Ireland and France (with PCI status) | 2026
| Greenlink Interconnector | Project providing interconnection to Great Britain (with PCI status) | 2024
| LirIC | Interconnector between Northern Ireland and Scotland | 2028
| MARES Connect | Interconnector between Ireland and Wales | 2027
3.6 Modelling of Non-Conventional Generation in Adequacy Studies
Table 3.8 - De-rating values used in AdCal studies
| Technology | De-rating value across 2022 - 2031
| Wind | 11% - 6%
| Solar | 13% - 5%
| Interconnectors | SEM <-> GB: 1000 MWrated * EMDF* with Outage Statistics
SEM <-> France: 700 MWrated * EMDF *with Outage Statistics
*Incorporates a 60% External Market De-Rating Factor (EMDF).
See Table 3.11 for outage statistics
3.7(a) Demand Side Units (DSUs)
Table 3.9 - Ireland and Northern Ireland DSU Capacity (MW rated)
|  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| Ireland | 604 | 639 | 589 | 727 | 662 | 662 | 662 | 662 | 662 | 662
| Northern Ireland | 143 | 136 | 165 | 225 | 234 | 234 | 234 | 234 | 234 | 234
| Total | 747 | 775 | 754 | 952 | 896 | 896 | 896 | 896 | 896 | 896
3.7(b) Energy Storage
Table 3.10 - Total battery capacity successful in auctions (MW rated) for Ireland and Northern Ireland
|  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| Ireland | 31 | 264 | 261 | 621 | 737 | 737 | 737 | 737 | 737 | 737
| Northern Ireland | 192 | 192 | 124 | 166 | 166 | 166 | 166 | 166 | 166 | 166
| Total | 223 | 456 | 385 | 787 | 903 | 903 | 903 | 903 | 903 | 903

## Generation - Availability
Generation Auction Results
3.1 Introduction
Figure 3.1 Age breakdown of dispatchable plant on the All-Island system
|  | Age | Capacity (MW)
| Thermal | <10 years | 525
|  | 10-19 years | 4024
|  | 20-29 years | 586
|  | 30-39 years | 1154
|  | >40 years | 1180
| Hydro | 8-59 years | 292
|  | 60-79 years | 130
|  | >80 years | 86
3.8 Plant Availability
Table 3.11– Summary of availability parameters used in the T-4 2025/2026 Capacity Market auction
| Technology Category | Mean Forced Outage Probability (%) | Mean Scheduled Outage Rate (weeks)
| DSU | 7.8% | 3
| Gas Turbine | 5.1% | 2
| Hydro | 4.5% | 6
| Steam Turbine | 14.2% | 3
| Pumped Storage | 7.4% | 3
| System Wide | 7.8% | 3
| Interconnector | 7.5% | 2
Figure 3.7- The average 365-day annual system-wide availability in Ireland and Northern Ireland
| Year | Availability (%) | 5 Year Average (%)
| 2010 | 86.6
| 2011 | 83.8
| 2012 | 87.2
| 2013 | 86.2
| 2014 | 83.1
| 2015 | 86.8
| 2016 | 86.2
| 2017 | 86.2 | 76.5
| 2018 | 79.9
| 2019 | 77
| 2020 | 74.9
| 2021 | 64.6
Figure 3.8 - Average annual system-wide Forced Outage Rates in Ireland for each of the past 13 years (solid lines in navy blue), and also across 2017-2021 (Dashed Orange) and 2013-2017 (Solid Red)
| Year | Forced Outage Rate (IE) (%) | 5 Year Average 2014-2018 (%) | 5 Year Average 2017-2021 (%)
| 2010 | 5.4
| 2011 | 8.9
| 2012 | 7.5
| 2013 | 7.3
| 2014 | 8.5 | 7.7
| 2015 | 6.6
| 2016 | 3
| 2017 | 8.8 |  | 15.1
| 2018 | 11.6
| 2019 | 14.8
| 2020 | 16.2
| 2021 | 24.1
Figure 3.9 - Average annual system-wide FOR in Northern Ireland for each of the past 13 years (solid lines in light blue), and also across 2017-2021 (Dashed Orange) and 2013-2017 (Solid Red)
| Year | Forced Outage Rate (NI) (%) | 5 Year Average 2014-2018 (%) | 5 Year Average 2017-2021 (%)
| 2010 | 7.6
| 2011 | 3.7
| 2012 | 8.9
| 2013 | 4.4
| 2014 | 4.3 | 7
| 2015 | 8.3
| 2016 | 5.9
| 2017 | 8.2 |  | 10.5
| 2018 | 8.5
| 2019 | 11
| 2020 | 13
| 2021 | 11.7
Figure 3.10- Ireland and Northern Ireland Conventional Unit Availability
| Date | Ireland (%) | Northern Ireland (%)
| 2018-01-01 | 89.9 | 95.3
| 2018-02-01 | 89.6 | 95
| 2018-03-01 | 89 | 94.8
| 2018-04-01 | 88.4 | 93.5
| 2018-05-01 | 88 | 93.1
| 2018-06-01 | 87.7 | 91.9
| 2018-07-01 | 87.5 | 90.6
| 2018-08-01 | 87.4 | 89.4
| 2018-09-01 | 88 | 88.2
| 2018-10-01 | 87.3 | 86.8
| 2018-11-01 | 86.6 | 85.9
| 2018-12-01 | 85.1 | 85.6
| 2019-01-01 | 83.8 | 84.3
| 2019-02-01 | 83.3 | 83.9
| 2019-03-01 | 82.9 | 84.3
| 2019-04-01 | 82.7 | 83.4
| 2019-05-01 | 82.6 | 83.6
| 2019-06-01 | 82.5 | 83.6
| 2019-07-01 | 82.2 | 83.6
| 2019-08-01 | 81.6 | 84
| 2019-09-01 | 80.7 | 84.9
| 2019-10-01 | 80.7 | 84.7
| 2019-11-01 | 81.6 | 84.6
| 2019-12-01 | 82.4 | 85.7
| 2020-01-01 | 83.2 | 84.4
| 2020-02-01 | 83.4 | 83.8
| 2020-03-01 | 83.5 | 83.8
| 2020-04-01 | 83.4 | 83.7
| 2020-05-01 | 83.6 | 84.2
| 2020-06-01 | 83.8 | 84.5
| 2020-07-01 | 83.6 | 84.1
| 2020-08-01 | 83.6 | 82.5
| 2020-09-01 | 83.9 | 82.5
| 2020-10-01 | 83.8 | 80.8
| 2020-11-01 | 83.5 | 79.4
| 2020-12-01 | 83.2 | 80.5
| 2021-01-01 | 82 | 80.7
| 2021-02-01 | 80.3 | 80.5
| 2021-03-01 | 78.8 | 80.1
| 2021-04-01 | 77 | 79.7
| 2021-05-01 | 74.5 | 79.5
| 2021-06-01 | 72.2 | 79.4
| 2021-07-01 | 70 | 80.6
| 2021-08-01 | 68.2 | 81.1
| 2021-09-01 | 65.9 | 81.5
| 2021-10-01 | 64.6 | 80.1
| 2021-11-01 | 63.5 | 78.7
| 2021-12-01 | 63.3 | 78

## Adequacy
Adequacy
4.1 Adequacy Results for Ireland
Table 4.1 - Results of adequacy studies for Ireland, given in MW of surplus plant (+) or deficit (-) Figure 4.1 – Core scenario adequacy results for Ireland, in terms of surplus or deficit of plant.
| Core Scenarios | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| Low Demand | -270 | -300 | -600 | -1090 | -900 | -720 | -790 | -790 | -810 | -930
| Median Demand | -380 | -530 | -940 | -1490 | -1280 | -1140 | -1280 | -1340 | -1420 | -1600
| High Demand | -510 | -720 | -1230 | -1820 | -1700 | -1660 | -1850 | -1930 | -2030 | -2220
Sensitivities on Median Demand
| No NS Availability | -480 | -630 | -1040 | -1590 | -1380 | -1240 | -1380 | -1440 | -1520 | -1700
| No ARHL | -380 | -530 | -940 | -1490 | -850 | -710 | -840 | -900 | -980 | -1170
| No ARHL, No Capacity Delays or Terminations | -380 | -530 | -840 | -470 | -410 | -360 | -490 | -540 | -620 | -830
| MP Available in 2025 | -380 | -530 | -940 | -1110 | -1280 | -1140 | -1280 | -1340 | -1420 | -1600
Table 4.2 - Loss of Load Expectation (LOLE) for Ireland in the median scenario
| LOLE | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| Median | 57 | 118 | 593 | 3475 | 2516 | 1567 | 2306 | 2705 | 3273 | 4693
4.4 Adequacy Results for Northern Ireland
Figure 4.2 Adequacy results for Northern Ireland, in terms of surplus or deficit of plant (MW) Table 4.3 - Results of adequacy studies for Northern Ireland, given in MW of surplus plant (+) or deficit (-)
| Scenario | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| Median Demand | 50 | 40 | -40 | -170 | 490 | 480 | 480 | 460 | 450 | 420
| Low Demand | 90 | 100 | 40 | -80 | 630 | 630 | 640 | 650 | 640 | 640
| High Demand | -10 | -40 | -130 | -290 | 350 | 320 | 300 | 260 | 220 | 170
Sensitivities on Median Demand
| No NS Reliance | -150 | -160 | -240 | -370 | 290 | 280 | 280 | 260 | 250 | 220
| No NS Reliance & ARHL from 2026 | -150 | -160 | -240 | -370 | -250 | -260 | -270 | -280 | -300 | -320
| Late Delivery | 50 | 40 | -150 | -170 | -80 | 480 | 480 | 460 | 450 | 420
Table 4.4 - Results of adequacy studies for Northern Ireland, given in Hrs of LOLE.
| LOLE | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| Median Demand | 2.9 | 3.1 | 7.8 | 31.1 | 0 | 0 | 0 | 0 | 0 | 0
4.5 Adequacy Results for the All-Island System
Figure 4.3 - Adequacy results for the All-Island system Table 4.5 - Results of adequacy studies for the All-Island system (MW)
| Scenario | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| Median Demand | -400 | -260 | -370 | -420 | -470 | -640
| Low Demand | 200 | 410 | 370 | 400 | 400 | 290
| High Demand | -960 | -900 | -1080 | -1160 | -1260 | -1460
Table 4.6 - Loss of Load Expectation (LOLE) for All-Island System (hours)
| LOLE | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| Median Demand | 60 | 30 | 49 | 62 | 79 | 164

## System Inputs - IE
Ireland Modelling Inputs
Ireland Demand
|  |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| GCS22 Median Transmission Peak Demand (MW) |  | 5730 | 5990 | 6250 | 6400 | 6450 | 6570 | 6680 | 6780 | 6870 | 6940
| Reserve Requirement (MW) |  | 375 | 375 | 375 | 375 | 375 | 525 | 525 | 525 | 525 | 525
| Transmission Outage Planning (MW) |  |  |  |  | 350 | 350 | 350 | 350 | 350 | 350 | 350
| Total (MW) |  | 6105 | 6365 | 6625 | 7125 | 7175 | 7445 | 7555 | 7655 | 7745 | 7815
Ireland Generation Portfolio Unit Capacities
The modelling of the system’s ability to meet the fluctuating demand is a complex function of combined probabilities of forced outage rates, optimisation of scheduled outage, annual run hour limitations and storage capacity and duration. As such, a simple comparison of the demand and total capacities here is not indicative of the adequacy position. The rated capacities and availabilities below are the inputs provided into that complex function.
|  |  | 2022: Rated Capacity (MW) | Forced Outage Rate | Scheduled Outage Duration (weeks)
|  | ID | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| Aghada | AT1 | 2022: 90; 2023: 90 | 0.36% | 1
|  | AT2 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 0.2% | 0
|  | AT4 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1.09% | 0
|  | AD2 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 5.52% | 10
| Ardnacrusha | AA1 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 0% | 1
|  | AA2 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 0% | 3
|  | AA3 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 1.9% | 1
|  | AA4 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 14.3% | 2
| Dublin Bay | DB1 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 3.88% | 4
| Dublin Waste | DW1 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 6.46% | 2
| Edenderry | ED1 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 |  | 2.14% | 9
|  | ED3 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 0.01% | 1
|  | ED5 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 0.04% | 1
| Erne | ER1 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 3% | 1
|  | ER2 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 5% | 1
|  | ER3 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 1.6% | 1
|  | ER4 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 0.7% | 3
| Great Island CCGT | GI4 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 11.83% | 1
| Huntstown | HNC | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 11.73% | 0
|  | HN2 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 7.27% | 3
| Indaver Waste | IW1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 8.06% | 2
| Lee | LE1 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 1.5% | 3
|  | LE2 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 7% | 2
|  | LE3 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0.3% | 2
| Liffey | LI1 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 3.9% | 1
|  | LI2 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 11.8% | 0
|  | LI3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 0.6% | 1
|  | LI4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 0.3% | 0
| Moneypoint | MP1 | 2022: 285; 2023: 285; 2024: 285 | 26.2% | 0
|  | MP2 | 2022: 250; 2023: 250; 2024: 250 | 37.84% | 6
|  | MP3 | 2022: 285; 2023: 285; 2024: 285 | 43.28% | 0
| Poolbeg CC | PBA | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 11.23% | 7
|  | PBB | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 18% | 2
| Rhode | RP1 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 6.45% | 0
|  | RP2 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 4.41% | 1
| Sealrock | SK3 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1.88% | 2
|  | SK4 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 0.14% | 3
| Tarbert | TB1 | [10 empty] | 1.13% | 1
|  | TB2 | [10 empty] | 3.53% | 1
|  | TB3 | 2022: 241; 2023: 241 | 18.81% | 1
|  | TB4 | [10 empty] | 4.7% | 1
| Tawnaghmore | TP1 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 0.04% | 0
|  | TP3 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 0.12% | 0
| Tynagh | TYC | 388 | 388 | 388 | 388 | 388 | 388 | 388 | 388 | 388 | 388 | 7.51% | 1
| Whitegate | WG1 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 2.53% | 2
| Turlough Hill | TH1 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 2.4% | 4
|  | TH2 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 4% | 4
|  | TH3 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 3.9% | 4
|  | TH4 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 0.2% | 4
| Industrial | INDU | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 91.7% | 0
| Small Scale Hydro | SSH | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 76.5% | 0
| Conventional CHP | CHP | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 37.45% | 0
| Landfill Gas | LFG | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 66.5% | 0
| CHP_Bio | CHP Bio | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 20% | 0
| Batteries | Batteries | 31[1] | 264[1] | 261[1] | 621[1] | 737[1] | 737[1] | 737[1] | 737[1] | 737[1] | 737[1] | 7.8%[4] | 3[4]
| DSU | DSU | 604[2] | 639[2] | 589[2] | 727[2] | 662[2] | 662[2] | 662[2] | 662[2] | 662[2] | 662[2] | 7.8%[4] | 3[4]
| Gas Turbine Auction Results |  |  |  | 120 | 310 | 1100[3] | 1240[3] | 1240[3] | 1240[3] | 1240[3] | 1240[3] | 5.1%[4] | 2[4]
| GB to IE Interconnection |  | 300[5] | 300[5] | 300[5] | 300[5] | 300[5] | 300[5] | 300[5] | 300[5] | 300[5] | 300[5] | 7.5%[4] | 2[4]
| FR to IE Interconnection |  | 2027: 420[5]; 2028: 420[5]; 2029: 420[5]; 2030: 420[5]; 2031: 420[5] | 7.5%[4] | 2[4]
[1] The contribution to system adequacy of battery storage is restricted by the size and duration. The average volume of storage of batteries on the system limits the duration of these units to 0.5 hours in 2022, up to 2.2 hours from 2026.
[2] Circa 80% of the DSU capacity noted here has limitations on how many hours per day it can be utilised, restricting the duration of which this capacity can be delivered, and thus it’s ability to meet demand and contribute to adequacy. The average run hour limitation of these units is 2.3 hours per day.
[3] Some of this capacity has annual run hour limitations as noted in Table 3.1 (Generation – Auction Results). This has been represented through modelling by restricting the number of hours of running available to a unit per year. For example a unit with a 1,500 Annual run hour limit is forced to be unavailable for 7,260 hours per year. Restricting the availability of this capacity reduces the system’s ability to meet demand.
[4] Outage rates for new units based on 5 year average as shown in Table 3.11 (Generation - Availability)
[5] Interconnector rated capacities incorporates 60% External Market Derating Factor
Ireland Generation Portfolio Capacity Credits
Capacity (MW)
| Source |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| Wind |  | 467 | 476 | 476 | 489 | 497 | 505 | 538 | 613 | 678 | 720
| Solar |  | 24 | 43 | 57 | 60 | 72 | 79 | 78 | 80 | 82 | 85
| NI Reliance |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100

## System Inputs - NI
Northern Ireland Modelling Inputs
Northern Ireland Demand
|  |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| GCS22 Median Transmission Peak Demand (MW) |  | 1640 | 1660 | 1680 | 1700 | 1750 | 1770 | 1790 | 1810 | 1830 | 1860
| Reserve Requirement (MW) |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
| Total (MW) |  | 1840 | 1860 | 1880 | 1900 | 1950 | 1970 | 1990 | 2010 | 2030 | 2060
Northern Ireland Generation Portfolio Unit Capacities
The modelling of the system’s ability to meet the fluctuating demand is a complex function of combined probabilities of forced outage rates, optimisation of scheduled outage, annual run hour limitations and storage capacity and duration. As such, a simple comparison of the demand and total capacities here is not indicative of the adequacy position. The rated capacities and availabilities below are the inputs provided into that complex function.
|  |  | 2022: Rated Capacity (MW) | Forced Outage Rate | Scheduled Outage Duration (weeks)
|  | ID | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| Ballylumford | B31 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 9.1% | 2
|  | B32 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 7.8% | 3
|  | B10 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 10.4% | 2
|  | GT7(GT1) | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 1.6% | 0
|  | GT8(GT2) | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 1.4% | 0
| Kilroot | ST1 | 2022: 130; 2023: 130 | 6.7% | 11
|  | ST2 | 2022: 130; 2023: 130 | 18.3% | 8
|  | KGT1 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 8.7% | 0
|  | KGT2 | 29 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 3.7% | 1
|  | KGT3 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 4.1% | 0
|  | KGT4 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 3.6% | 0
| Coolkeeragh | GT8 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 3.3% | 5
|  | C30 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 3.8% | 2
| AGU | AGU | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 2.9% | 3
| Lisahally | Lisahally | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17.2% | 4
| Contour Global | CGA | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 4.8% | 0
|  | CGC | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4.8% | 0
| CHP | NI_CHP | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 39% | 0
| Biogass | NI_BIOGAS | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 56% | 0
| Biomass | NI_BIOMASS | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 70.3% | 0
| Renewable CHP | NI_CHP_RES | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 39.5% | 0
| Hydro | NI_SSH | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 67% | 0
| Landfill Gas | NI_LFG | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 46.1% | 0
| Diesel | NI_DIESEL | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 87.5% | 0
| Batteries | Batteries | 192[1] | 192[1] | 124[1] | 166[1] | 166[1] | 166[1] | 166[1] | 166[1] | 166[1] | 166[1] | 7.8%[4] | 3[4]
| DSU | DSU | 143[2] | 136[2] | 165[2] | 225[2] | 234[2] | 234[2] | 234[2] | 234[2] | 234[2] | 234[2] | 7.8%[4] | 3[4]
| Gas Turbine Auction Results |  |  |  | 720[3] | 720[3] | 720 | 720 | 720 | 720 | 720 | 720 | 5.1%[4] | 2[4]
| Steam Turbine Auction Results | [5 empty] | 310 | 310 | 310 | 310 | 310 | 310 | 14.2%[4] | 3[4]
| GB to NI Interconnection |  | 300[5] | 300[5] | 300[5] | 300[5] | 300[5] | 300[5] | 300[5] | 300[5] | 300[5] | 300[5] | 7.5%[4] | 2[4]
[1] The contribution to system adequacy of battery storage is restricted by the size and duration. The average volume of storage of batteries on the system limits the duration of these units to 0.5 hours in 2022, up to 2.2 hours from 2026.
[2] Circa 80% of the DSU capacity noted here has limitations on how many hours per day it can be utilised, restricting the duration of which this capacity can be delivered, and thus it’s ability to meet demand and contribute to adequacy. The average run hour limitation of these units is 2.3 hours per day.
[3] Some of this capacity has annual run hour limitations as noted in Table 3.1 (Generation – Auction Results). This has been represented through modelling by restricting the number of hours of running available to a unit per year. For example a unit with a 1,500 Annual run hour limit is forced to be unavailable for 7,260 hours per year. Restricting the availability of this capacity reduces the system’s ability to meet demand.
[4] Outage rates for new units based on 5 year average as shown in Table 3.11 (Generation - Availability)
[5] Interconnector rated capacities incorporates 60% External Market Derating Factor
Northern Ireland Generation Portfolio RES Capacity Credits
Capacity (MW)
| Source |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031
| Wind |  | 171 | 177 | 173 | 176 | 167 | 172 | 176 | 179 | 183 | 184
| Solar |  | 25 | 24 | 29 | 28 | 35 | 38 | 41 | 46 | 45 | 46
| IE Reliance |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200