## Front Page
2023 - 2032 All Island Generation Capacity Statement Data Workbook
Purpose: To publically share the data used throughout the Generation Capacity Statement 2023-2032. For any questions on this data, please contact info@EirGrid.com or info@SONI.ltd.uk, referencing the GCS 2023-2032 in the subject line.
Disclaimer: EirGrid Plc and SONI Ltd have followed accepted industry practice in the collection and analysis of data available. While all reasonable care has been taken in the preparation of this data, EirGrid and SONI are not responsible for any loss that may be attributed to the use of this information. Prior to taking business decisions, interested parties are advised to seek separate and independent opinion in relation to the matters covered by this report and should not rely solely upon data and information contained herein. Information in this document does not amount to a recommendation in respect of any possible investment. This document does not purport to contain all the information that a prospective investor or participant in the Single Electricity Market (SEM) may need.
Version History:
| Version | Description | Date
| 1 | Initial Publication | 2024-01-11
Contents (In order shown in report):
| Location in Report | Description | Link
| Table 4.1 | Average annual growths for macroeconomic parameters, values used for Median demand as advised by the ESRI. | Demand IE
| Table 4.2 | Forecasted Data Centre and New Technology Load Demand by 2032. 2022 Demand 734 MVA. | Demand IE
| Figure 4.1 | Ireland demand expected from assumed build out of data centres and new technology loads. | Demand IE
| Table 4.3 | Climate Action Plan 2023 targets for Electric Vehicles and Heat Pumps | Demand IE
| Figure 4.2 | Electric Vehicle Electrical Energy Demand - Median Scenario | Demand IE
| Figure 4.3 | Heat Pump Electrical Energy Demand - Median Scenario | Demand IE
| Figure 4.7 | Total Electricity Requirement for Ireland | Demand IE
| Table 4.4 | Low, Median and High Total Electricity Requirement Key Assumption Differences | Demand IE
| Figure 4.8 | Ireland Median Demand Total Electricity Requirement Sectoral Breakdown | Demand IE
| Figure 4.9 | Ireland Median Demand Sectoral Proportion of Energy Requirement | Demand IE
| Figure 4.4 | Historic Recorded and Temperature Corrected Peak Demand | Demand IE
| Figure 4.5 | Impact of Demand Flexibility on 2030 Peak Day (Median Scenario) | Demand IE
| Figure 4.6 | Impact of Demand Flexibility in median scenario across the study period | Demand IE
| Figure 4.10 | Transmission Peak Forecast for Ireland | Demand IE
| Table 4.5 | Low, Median and High Peak Demand Key Assumption Differences | Demand IE
| Figure 4.11 | Residential, Commercial and Industrial Peak Demand (excluding electric vehicles, heat pumps, data centres and new technology loads) | Demand IE
| Table 4.6 | Number of electric vehicles and Heat Pump installations included in the low, median, and high demand forecast. | Demand NI
| Figure 4.12 | Northern Ireland TER Forecast | Demand NI
| Figure 4.13 | The TER demand forecast built up from the various demand components for the years 2025 and 2030 | Demand NI
| Table 4.7 | Low, Median and High Total Electricity Requirement Key Assumption Differences | Demand NI
| Figure 4.14 | ACS Transmission Peak Forecasts for Northern Ireland | Demand NI
| Table 4.8 | Low, Median and High Peak Demand Key Assumption Differences | Demand NI
| Figure 4.15 | Impact of Demand Flexibility on 2030 Peak Day (Median Scenario) | Demand NI
| Figure 4.16 | Impact of Demand Flexibility in median scenario across the study period | Demand NI
| Figure 4.17 | Combined TER Forecast for the All-Island System | Demand AI
| Figure 4.18 | TER Peak for the Combined All-Island Forecast | Demand AI
| Figure 5.1 | Age breakdown of dispatchable plant on the All-Island system as of 2023 | Generation - Availability
| Figure 5.2 | All-Island derated successful new capacity in the T-4 2026-2027 Capacity Auction (non-risk adjusted) | Generation - Auction Results
| Table 5.1 | Ireland assumptions for new conventional plant capacities in adequacy studies (rated MW) | Generation - Auction Results
| Table 5.2 | Northern Ireland assumptions for new conventional plant capacities in adequacy studies (rated MW) | Generation - Auction Results
| Table 5.3 | Assumptions for conventional plant changes in Ireland | Generation - Conventional IE
| Table 5.4 | Assumptions for Kilroot GT plant capacity | Generation - Conventional NI
| Table 5.5 | Assumptions for plant changes in Northern Ireland | Generation - Conventional NI
| Table 5.6 | Capacity reliance at present on the existing North South Interconnector | Generation - Non-Conventional
| Table 5.7 | Future Interconnection Projects | Generation - Non-Conventional
| Figure 5.3 | Assumed growth of renewable capacity in Ireland. | Generation - Renewable IE
| Figure 5.4 | The actual and normalised energy produced from wind power in Ireland over the last ten years. | Generation - Renewable IE
| Figure 5.5 | The actual and normalised energy produced from wind power in Northern Ireland over the last ten years. | Generation - Renewable NI
| Figure 5.6 | Assumed growth of renewable capacity in Northern Ireland | Generation - Renewable NI
| Figure 5.7 | Impact of Solar Using Net Demand Methodology in Ireland in 2030 | Generation - Non-Conventional
| Figure 5.8 | Impact of Solar Using Net Demand Methodology in Northern Ireland in 2030 | Generation - Non-Conventional
| Figure 5.9 | Impact of Wind Using Net Demand Methodology in Ireland in 2030 | Generation - Non-Conventional
| Figure 5.10 | Impact of Wind Using Net Demand Methodology in Northern Ireland in 2030 | Generation - Non-Conventional
| Table 5.8 | Derating values used in AdCal Studies | Generation - Non-Conventional
| Table 5.9 | Ireland and Northern Ireland DSU Capacity (MW rated) | Generation - Non-Conventional
| Table 5.10 | Total Storage Generation Capacity (MW rated) assumed in studies for Ireland and Northern Ireland | Generation - Non-Conventional
| Table 5.11 | Total Energy Storage Storage Capacity (MWh) assumed in studies for Ireland and Northern Ireland | Generation - Non-Conventional
| Table 5.12 | Summary of availability parameters used in the study | Generation - Availability
| Figure 5.11 | All-island average annual conventional generation capacity availability for the past 10 years (excluding DSU) | Generation - Availability
| Figure 5.12 | Average annual conventional generation capacity Forced Outage Rates in Ireland for the past 10 years (excluding DSU) | Generation - Availability
| Figure 5.13 | Average annual conventional generation capacity Forced Outage Rates in Northern Ireland for the past 10 years (excluding DSU) | Generation - Availability
| Figure 5.14 | Ireland and Northern Ireland Conventional Generation Capacity Availability for the last 5 years (excluding DSU) | Generation - Availability
| Figure 5.15 | All-Island Demand Side Unit Monthly Availability for 2022 Calendar year | Generation - Availability
| Table 6.1 | Results of adequacy studies for Ireland given in MW of surplus plant (+) or deficit (-) | Adequacy
| Figure 6.1 | Core scenario adequacy analysis for Ireland in terms of surplus (+) and deficit (-) of plant | Adequacy
| Table 6.2 | Loss of Load Expectation (LOLE) in hours for Ireland in the median scenario. Previous reported LOLE included operational requirements. | Adequacy
| Figure 6.2 | Ireland Adequacy Position with Mitigating Measures | Adequacy
| Figure 6.3 | Adequacy results for Northern Ireland, in terms of surplus (+) or deficit (-) of plant (MW) | Adequacy
| Table 6.3 | Results of adequacy studies for Northern Ireland, given in ME of surplus plant (+) or deficit (-) | Adequacy
| Table 6.4 | Results of adequacy studies for Northern Ireland, given in hours of LOLE. Previous reported LOLE included operational requirements. | Adequacy
| Figure 6.4 | Adequacy Results for the All-Island System | Adequacy
| Table 6.5 | Results of adequacy studies for the All-Island system (MW) | Adequacy
| Table 6.6 | Loss of Load Expectation (LOLE) for All-Island System (hours) | Adequacy
| Table A2-1 | Capacity Market Auction Results | Generation Auction Results
| Table A2-2 | Units issued with Termination Notices since 2021 in addition to those identified in GCS 2021 | Generation Auction Results
| Table A4-1 | Registered Capacity of dispatchable generation and interconnectors in Ireland in 2023 (MW) DSU: Demand Side Unit; HFO: Heavy Fuel Oil; DO: Distillate Oil | Generation Conventional IE
| Table A4-2 | Partially/Non-Dispatchable plant in Ireland (MW) | Generation Renewable IE
| Table A4-3 | All Renewable energy sources in Ireland (MW). We have assumed that the peat plant at Edenderry will be approximately 60% powered by biomass by 2023 and 100% biomass from 2024 | Generation Renewable IE
| Table A4-4 | Registered Capacity of dispatchable generation and interconnectors in Northern Ireland in 2023 (MW). | Generation Conventional NI
| Table A4-5 | Partially/Non-Dispatchable plant in Northern Ireland (MW). | Generation Renewable NI
| Table A4-6 | All Renewable energy sources in Northern Ireland (MW). | Generation Renewable NI

## Demand - IE
Demand Forecast for Ireland
2.2(c) Forecasting Causal Inputs
Table 4.1 - Average annual growths for macroeconomic parameters, values used for Median demand as advised by the ESRI.
|  | 2022-2023 |  |  | 2024-2032
|  | Low (75% ESRI) | Median (ESRI) | High (110% ESRI) | Low (75% ESRI) | Median (ESRI) | High (110% ESRI)
| Real GNI* | 0.15% | 0.2% | 0.22% | 2.25% | 3% | 3.3%
| Personal Consumption | 3% | 4% | 4.4% | 1.88% | 2.5% | 2.75%
2.2(d) Forecasting Data Centres and New Technology Loads in Ireland
Table 4.2 - Forecasted Data Centre and New Technology Load Demand by 2032. 2022 Demand 734 MVA.
| Forecast Scenario | Growth from 2022-2032 (MVA) | 2032 Demand (MVA)
| Low | 304 | 1038
| Median | 810 | 1543
| High | 1276 | 2010
Figure 4.1 - Ireland demand expected from assumed build out of data centres and new technology loads.
| Year | Historical (MVA) | Contract Ramp (MVA) | Low Scenario (MVA) | Median Scenario (MVA) | High Scenario (MVA)
| 2016 | 196.5 | 360
| 2017 | 262 | 528
| 2018 | 357.2 | 611
| 2019 | 431.5 | 698
| 2020 | 519.8 | 884
| 2021 | 600.1 | 1015
| 2022 | 733.5 | 1325
| 2023 |  | 1730 | 795 | 895 | 971
| 2024 |  | 1856 | 844 | 1013 | 1220
| 2025 |  | 2006 | 865 | 1117 | 1383
| 2026 |  | 2162 | 902 | 1224 | 1547
| 2027 |  | 2203 | 945 | 1282 | 1709
| 2028 |  | 2237 | 963 | 1340 | 1801
| 2029 |  | 2273 | 984 | 1394 | 1869
| 2030 |  | 2273 | 1004 | 1449 | 1921
| 2031 |  | 2273 | 1022 | 1498 | 1966
| 2032 |  | 2273 | 1038 | 1543 | 2010
2.2(e) Forecast Scenarios and Climate Action Plan
Table 4.3 - Climate Action Plan 2023 targets for Electric Vehicles and Heat Pumps
|  | Electric Vehicles |  |  | Heat Pump Installations
|  | Passenger | Commercial |  | Residential - New Builds | Residential - Retrofits | Commercial
| 2025 | 175000 | 20000 |  | 100000 | 100000 | N/A
| 2030 | 845000 | 95000 |  | 250000 | 400000 | 50000
Figure 4.2 - Electric Vehicle Electrical Energy Demand - Median Scenario
| Year | BEVs (TWh) | PHEVs (TWh) | Commercial (TWh) | Total (TWh)
| 2021 | 0.06 | 0.02 | 0.01 | 0.1
| 2022 | 0.11 | 0.04 | 0.02 | 0.16
| 2023 | 0.12 | 0.06 | 0.02 | 0.19
| 2024 | 0.19 | 0.09 | 0.04 | 0.31
| 2025 | 0.32 | 0.12 | 0.07 | 0.52
| 2026 | 0.5 | 0.15 | 0.13 | 0.77
| 2027 | 0.71 | 0.18 | 0.19 | 1.08
| 2028 | 0.95 | 0.22 | 0.27 | 1.43
| 2029 | 1.21 | 0.25 | 0.35 | 1.81
| 2030 | 1.49 | 0.28 | 0.44 | 2.21
| 2031 | 1.87 | 0.33 | 0.56 | 2.76
| 2032 | 2.29 | 0.38 | 0.69 | 3.35
Figure 4.3 - Heat Pump Electrical Energy Demand - Median Scenario
| Year | New Builds - Residential (TWh) | Retrofits - Residential (TWh) | Commercial (TWh) | Total (TWh)
| 2021 | 0.22 | 0.06 | 0.33 | 0.61
| 2022 | 0.25 | 0.07 | 0.36 | 0.68
| 2023 | 0.32 | 0.09 | 0.38 | 0.78
| 2024 | 0.41 | 0.11 | 0.46 | 0.98
| 2025 | 0.54 | 0.14 | 0.59 | 1.27
| 2026 | 0.63 | 0.25 | 0.74 | 1.62
| 2027 | 0.71 | 0.4 | 0.9 | 2
| 2028 | 0.77 | 0.59 | 0.99 | 2.35
| 2029 | 0.8 | 0.84 | 1.04 | 2.69
| 2030 | 0.81 | 1.15 | 1.06 | 3.03
| 2031 | 0.95 | 1.36 | 1.11 | 3.42
| 2032 | 1.09 | 1.56 | 1.15 | 3.8
2.2(f) Total Electricity Requirement (TER)
Figure 4.7 – Total Electricity Requirement for Ireland
|  | Historical (TWh) | GCS23 (TWh) |  |  | GCS22 (TWh)
| Year |  | GCS Low | GCS Median | GCS High | Low | Median | High
| 2016 | 28.27
| 2017 | 29.15
| 2018 | 29.91
| 2019 | 30.47
| 2020 | 30.7
| 2021 | 32.15 | 32.15 | 32.15 | 32.15 | 31.71 | 31.71 | 31.71
| 2022 |  | 33.3 | 33.34 | 33.36 | 33.01 | 33.74 | 34.37
| 2023 |  | 34.26 | 34.88 | 35.3 | 34.1 | 35.71 | 37.23
| 2024 |  | 34.95 | 36.48 | 37.92 | 35.42 | 37.52 | 40.06
| 2025 |  | 35.58 | 38 | 40.39 | 36.04 | 38.49 | 41.57
| 2026 |  | 36.24 | 39.58 | 42.59 | 36.96 | 39.89 | 43.63
| 2027 |  | 37.08 | 41.03 | 44.89 | 37.77 | 41.29 | 45.57
| 2028 |  | 37.83 | 42.27 | 46.87 | 38.64 | 42.73 | 47.44
| 2029 |  | 38.49 | 43.5 | 48.41 | 39.26 | 43.89 | 48.81
| 2030 |  | 39.17 | 44.73 | 49.79 | 39.96 | 45.06 | 50.14
| 2031 |  | 40.02 | 46.17 | 51.31 | 40.6 | 46.1 | 51.17
| 2032 |  | 40.9 | 47.62 | 52.86
Table 4.4 - Low, Median and High Total Electricity Requirement Key Assumption Differences
|  | Low | Median | High
| Number of Electric Vehicles | 75% Climate Action Plan Targets | 100% Climate Action Plan Targets | 110% Climate Action Plan Targets
| Number of Domestic and Commercial Heat Pumps | 75% Climate Action Plan Targets | 100% Climate Action Plan Targets | 110% Climate Action Plan Targets
| Data Centre and New Technology Loads | Low Ramp | Median Ramp | High Ramp
| Economic Growth Projection | 75% ESRI Economic Projection | 100% ESRI Economic Projection | 110% ESRI Economic Projection
Figure 4.8 - Ireland Median Demand Total Electricity Requirement Sectoral Breakdown
|  | Residential (TWh) | Commercial (TWh) | Industrial (TWh) | Electric Vehicles (TWh) | Heat Pumps (TWh) | Data Centres & New Tech Loads (TWh) | TER incorporating losses (TWh)
| 2018 | 8.5734 | 9.3526 | 7.0555 | 0.01425 | 0.31559 | 2.7
| 2019 | 8.4876 | 9.1698 | 6.9176 | 0.028531 | 0.39847 | 3.45
| 2020 | 8.9945 | 8.4431 | 6.3694 | 0.051074 | 0.51604 | 4.16
| 2021 | 9.0341 | 8.753 | 6.6031 | 0.096552 | 0.61472 | 4.89 | 32.15
| 2022 | 9.1125 | 8.7424 | 6.5951 | 0.16341 | 0.67767 | 5.83 | 33.34
| 2023 | 9.1478 | 8.7317 | 6.5871 | 0.19483 | 0.78231 | 7.11 | 34.88
| 2024 | 9.1164 | 8.7267 | 6.5833 | 0.31379 | 0.98373 | 8.33 | 36.48
| 2025 | 9.0827 | 8.7216 | 6.5795 | 0.51814 | 1.2707 | 9.3 | 38
| 2026 | 9.0469 | 8.7166 | 6.5757 | 0.77447 | 1.6164 | 10.23 | 39.58
| 2027 | 9.0088 | 8.7115 | 6.5719 | 1.0833 | 1.9995 | 10.95 | 41.03
| 2028 | 8.9683 | 8.7065 | 6.568 | 1.4332 | 2.3521 | 11.46 | 42.27
| 2029 | 8.9255 | 8.7014 | 6.5642 | 1.8134 | 2.6893 | 11.95 | 43.5
| 2030 | 8.8803 | 8.6964 | 6.5604 | 2.213 | 3.0278 | 12.42 | 44.73
| 2031 | 8.8574 | 8.6913 | 6.5566 | 2.7552 | 3.4153 | 12.88 | 46.17
| 2032 | 8.8318 | 8.6863 | 6.5528 | 3.3548 | 3.8029 | 13.29 | 47.62
Figure 4.9 - Ireland Median Demand Sectoral Proportion of Energy Requirement
|  | 2022 (TWh) | 2032 (TWh)
| Residential | 9.03 | 8.83
| Electric Vehicles | 0.1 | 3.35
| Heat Pumps | 0.61 | 3.8
| Commercial | 8.75 | 8.69
| Industrial | 6.6 | 6.55
| Data Centres & New Technology Loads | 4.89 | 13.29
2.2(g) Peak Demand Forecasting – Temperature Correction
Figure 4.4 - Historic Recorded and Temperature Corrected Peak Demand
| Year | Network Exported Peak (MW) | Historic Temperature-Corrected Peak (MW)
| 2002/03 | 4254 | 4330
| 2003/04 | 4184 | 4270
| 2004/05 | 4379 | 4560
| 2005/06 | 4667 | 4850
| 2006/07 | 4864 | 5020
| 2007/08 | 4914 | 5110
| 2008/09 | 4891 | 4900
| 2009/10 | 4992 | 4870
| 2010/11 | 5090 | 4900
| 2011/12 | 4640 | 4820
| 2012/13 | 4589 | 4730
| 2013/14 | 4523 | 4800
| 2014/15 | 4695 | 4890
| 2015/16 | 4668 | 4970
| 2016/17 | 4752 | 4970
| 2017/18 | 4940 | 5050
| 2018/19 | 4910 | 5180
| 2019/20 | 5007 | 5150
| 2020/21 | 5335 | 5370
| 2021/22 | 5346 | 5530
| 2022/23 | 5508 | 5470
2.2(h) Peak Demand Forecasting – Impact of ‘Smartness’
Figure 4.5 - Impact of Demand Flexibility on 2030 Peak Day (Median Scenario)
| Hr | No Flexibility Services or Incentives (MW) | 8% Residential Demand Reduction from Flexibility Services & Incentives (MW) | 8% Residential Demand Reduction and Flexible EV Charging Profile (MW)
| 0 | 5010 | 5010 | 5380
| 1 | 4780 | 4780 | 5240
| 2 | 4640 | 4640 | 5140
| 3 | 4580 | 4580 | 5100
| 4 | 4710 | 4710 | 5120
| 5 | 4950 | 4950 | 5210
| 6 | 5430 | 5430 | 5560
| 7 | 6130 | 6130 | 6070
| 8 | 6500 | 6500 | 6320
| 9 | 6700 | 6700 | 6460
| 10 | 6520 | 6520 | 6450
| 11 | 6450 | 6450 | 6420
| 12 | 6430 | 6430 | 6400
| 13 | 6400 | 6400 | 6350
| 14 | 6410 | 6410 | 6370
| 15 | 6490 | 6490 | 6440
| 16 | 6970 | 6900 | 6680
| 17 | 7310 | 7160 | 6850
| 18 | 7350 | 7200 | 6780
| 19 | 7130 | 7060 | 6630
| 20 | 6670 | 6670 | 6430
| 21 | 6400 | 6400 | 6230
| 22 | 6010 | 6010 | 5910
| 23 | 5750 | 5750 | 5730
Figure 4.6 - Impact of Demand Flexibility in median scenario across the study period
| Year | No Flexibility Services or Incentives (MW) | 8% Residential Demand Reduction from Flexibility Services & Incentives (MW) | 8% Residential Demand Reduction and Flexible EV Charging Profile (MW)
| 2023 | 5920 | 5880 | 5870
| 2024 | 6100 | 6050 | 6030
| 2025 | 6320 | 6250 | 6190
| 2026 | 6560 | 6470 | 6370
| 2027 | 6770 | 6670 | 6510
| 2028 | 6980 | 6870 | 6620
| 2029 | 7190 | 7060 | 6720
| 2030 | 7420 | 7270 | 6850
| 2031 | 7680 | 7530 | 7010
| 2032 | 7950 | 7800 | 7170
2.2(i) Peak Demand Forecasting – Overall
Figure 4.10 - Transmission Peak Forecast for Ireland
|  | Historical (MW) | GCS23 (MW) |  |  | GCS22 (MW)
| Year |  | Low | Median | High | Low | Median | High
| 2016 | 4903
| 2017 | 5017
| 2018 | 5126
| 2019 | 5112
| 2020 | 5341
| 2021 | 5507 |  |  |  | 5530 | 5530 | 5530
| 2022 | 5474 | 5474 | 5474 | 5474 | 5580 | 5730 | 5910
| 2023 |  | 5480 | 5740 | 5930 | 5680 | 5990 | 6190
| 2024 |  | 5530 | 5900 | 6240 | 5780 | 6250 | 6540
| 2025 |  | 5580 | 6070 | 6490 | 5810 | 6400 | 6710
| 2026 |  | 5650 | 6250 | 6750 | 5820 | 6450 | 6860
| 2027 |  | 5720 | 6380 | 7010 | 5860 | 6570 | 7040
| 2028 |  | 5760 | 6500 | 7170 | 5890 | 6680 | 7190
| 2029 |  | 5790 | 6600 | 7310 | 5920 | 6780 | 7310
| 2030 |  | 5850 | 6730 | 7450 | 5940 | 6870 | 7420
| 2031 |  | 5930 | 6880 | 7630 | 5950 | 6940 | 7490
| 2032 |  | 6020 | 7040 | 7810
Table 4.5 - Low, Median and High Peak Demand Key Assumption Differences
|  | Low | Median | High
| Number of Electric Vehicles | 75% Climate Action Plan Targets | 100% Climate Action Plan Targets | 110% Climate Action Plan Targets
| Number of Domestic and Commercial Heat Pumps | 75% Climate Action Plan Targets | 100% Climate Action Plan Targets | 110% Climate Action Plan Targets
| Data Centre and New Technology Loads | Low Ramp | Median Ramp | High Ramp
| Economic Growth Projection | 75% ESRI Economic Projection | 100% ESRI Economic Projection | 110% ESRI Economic Projection
Figure 4.11 - Residential, Commercial and Industrial Peak Demand (excluding electric vehicles, heat pumps, data centres and new technology loads)
|  | Historical (MW) | GCS23 (MW)
| Year |  | Low | Median | High
| 2011 | 4995
| 2012 | 4900
| 2013 | 4911
| 2014 | 4937
| 2015 | 4995
| 2016 | 4780
| 2017 | 4821
| 2018 | 4800
| 2019 | 4708
| 2020 | 4816
| 2021 | 4870
| 2022 | 4676 | 4676 | 4676 | 4676
| 2023 |  | 4610 | 4760 | 4860
| 2024 |  | 4570 | 4740 | 4860
| 2025 |  | 4530 | 4720 | 4850
| 2026 |  | 4500 | 4700 | 4840
| 2027 |  | 4460 | 4680 | 4830
| 2028 |  | 4430 | 4660 | 4820
| 2029 |  | 4390 | 4640 | 4810
| 2030 |  | 4360 | 4620 | 4810
| 2031 |  | 4340 | 4620 | 4820
| 2032 |  | 4330 | 4620 | 4830
Data Centre Demand
|  | Historical (MW) | GCS23 (MW)
| Year |  | Low | Median | High
| 2016 | 134
| 2017 | 174
| 2018 | 256
| 2019 | 319
| 2020 | 410
| 2021 | 490
| 2022 | 601
| 2023 |  | 662 | 737 | 838
| 2024 |  | 701 | 837 | 1046
| 2025 |  | 722 | 905 | 1185
| 2026 |  | 741 | 964 | 1300
| 2027 |  | 759 | 1022 | 1399
| 2028 |  | 778 | 1080 | 1491
| 2029 |  | 798 | 1134 | 1559
| 2030 |  | 819 | 1189 | 1611
| 2031 |  | 836 | 1238 | 1656
| 2032 |  | 853 | 1283 | 1700
*Note, for the purposes of forecasting, the GCS assumes unity power factor (1 MVA = 1 MW)

## Demand - NI
Demand Forecast for Northern Ireland
2.3(b) Demand Scenarios
Table 4.6 - Number of electric vehicles and Heat Pump installations included in the low, median, and high demand forecast.
|  | Low |  | Median |  | High
|  | Electric Vehicles | Heat Pump Installations | Electric Vehicles | Heat Pump Installations | Electric Vehicles | Heat Pump Installations
| 2025 | 73000 | 15000 | 100000 | 22000 | 101000 | 25000
| 2030 | 250000 | 80000 | 300000 | 120000 | 320000 | 140000
2.3(d) TER Forecast
Figure 4.12 - Northern Ireland TER Forecast
| Year | Historical (TWh) | GCS22 Median (TWh) | GCS23 Low (TWh) | GCS23 Median (TWh) | GCS23 High (TWh)
| 2017 | 8.77
| 2018 | 8.97
| 2019 | 8.71
| 2020 | 8.33
| 2021 | 8.56 | 8.56
| 2022 | 8.35 | 8.75 | 8.35 | 8.35 | 8.35
| 2023 |  | 8.92 | 8.12 | 8.41 | 8.52
| 2024 |  | 9.1 | 8.15 | 8.62 | 8.92
| 2025 |  | 9.27 | 8.35 | 8.88 | 9.38
| 2026 |  | 9.61 | 8.51 | 9.16 | 9.77
| 2027 |  | 9.74 | 8.67 | 9.66 | 10.42
| 2028 |  | 9.87 | 8.74 | 9.8 | 10.66
| 2029 |  | 10.02 | 8.81 | 9.98 | 10.96
| 2030 |  | 10.17 | 8.9 | 10.17 | 11.26
| 2031 |  | 10.41 | 8.9 | 10.43 | 11.49
| 2032 |  |  | 8.9 | 10.76 | 11.81
Figure 4.13 - Illustrates how the TER demand forecast is built up from the various demand components for the years 2025 and 2030. Growth in TER from 2025 is primarily driven by the electrification of heat and transport with government policies and incentives expected to drive growth.
|  | Transport (TWh) | Residential (TWh) | Industrial (TWh) | Tertiary (TWh) | Losses (TWh) | Total (TWh)
| 2025 | 0.23 | 2.69 | 3.23 | 1.83 | 0.97 | 8.96
| 2030 | 0.75 | 2.86 | 3.67 | 1.87 | 1.07 | 10.21
Table 4.7- Low, Median and High Total Electricity Requirement Key Assumption Differences
|  |  | Low | Median | High
| Number of Electric Vehicles |  | NIEN RP7 Projections | NIEN RP7 Projections | NIEN RP7 Projections
| Number of Heat Pumps |  | NIEN RP7 Projections | NIEN RP7 Projections | NIEN RP7 Projections
| Data Centre and New Technology Loads |  | None | Median Ramp | High Ramp
| Economic Growth Projection |  | Oxford Economics Ten Year Forecast Less 1% | Oxford Economics Ten Year Forecast | Oxford Economics Ten Year Forecast Plus 1%
| Temperature |  | One in 25 Year Mild | Seven Year Average | One in 25 Year Cold
2.3(e) Peak Demand Forecasting
Figure 4.14 - ACS Transmission Peak Forecasts for Northern Ireland
| Year | Historical (GW) | GCS21 Median (GW) | GCS22 Low (GW) | GCS22 Median (GW) | GCS22 High (GW)
| 2018 | 1.68
| 2019 | 1.71
| 2020 | 1.63
| 2021 | 1.62
| 2022 | 1.62 | 1.64
| 2023 |  | 1.66 | 1.49 | 1.56 | 1.64
| 2024 |  | 1.68 | 1.49 | 1.6 | 1.72
| 2025 |  | 1.7 | 1.52 | 1.64 | 1.78
| 2026 |  | 1.75 | 1.54 | 1.68 | 1.85
| 2027 |  | 1.77 | 1.6 | 1.75 | 1.87
| 2028 |  | 1.79 | 1.61 | 1.78 | 1.9
| 2029 |  | 1.81 | 1.62 | 1.8 | 1.95
| 2030 |  | 1.83 | 1.64 | 1.83 | 1.99
| 2031 |  | 1.86 | 1.64 | 1.85 | 2.03
| 2032 |  | 0 | 1.64 | 1.9 | 2.07
Table 4.8 - Low, Median and High Peak Demand Key Assumption Differences
|  |  | Low | Median | High
| Number of Electric Vehicles |  | NIEN RP7 Projections | NIEN RP7 Projections | NIEN RP7 Projections
| Number of Heat Pumps |  | NIEN RP7 Projections | NIEN RP7 Projections | NIEN RP7 Projections
| Data Centre and New Technology Loads |  | None | Median Ramp | High Ramp
| Economic Growth Projection |  | Oxford Economics Ten Year Forecast Less 1% | Oxford Economics Ten Year Forecast | Oxford Economics Ten Year Forecast Plus 1%
| Temperature |  | One in 25 Year Mild | Seven Year Average | One in 25 Year Cold
Figure 4.15 - Impact of Demand Flexibility on 2030 Peak Day (Median Scenario)
|  | Smart EV Charging (MW) | No Flexibility Services or Incentives (MW)
| 1 | 1090 | 1050
| 2 | 1080 | 1020
| 3 | 1060 | 990
| 4 | 1040 | 960
| 5 | 1050 | 980
| 6 | 1080 | 1020
| 7 | 1190 | 1160
| 8 | 1390 | 1390
| 9 | 1530 | 1550
| 10 | 1600 | 1630
| 11 | 1630 | 1650
| 12 | 1650 | 1670
| 13 | 1660 | 1680
| 14 | 1630 | 1640
| 15 | 1610 | 1620
| 16 | 1640 | 1650
| 17 | 1750 | 1780
| 18 | 1860 | 1910
| 19 | 1740 | 1810
| 20 | 1640 | 1690
| 21 | 1550 | 1590
| 22 | 1430 | 1460
| 23 | 1300 | 1310
| 24 | 1160 | 1150
Figure 4.16 - Impact of Demand Flexibility in median scenario across the study period
|  | Smart EV Charging (MW) | No Flexibility Services or Incentives (MW)
| 2023 | 1600 | 1610
| 2024 | 1640 | 1650
| 2025 | 1690 | 1710
| 2026 | 1730 | 1760
| 2027 | 1800 | 1840
| 2028 | 1820 | 1870
| 2029 | 1850 | 1910
| 2030 | 1870 | 1930
| 2031 | 1890 | 1960
| 2032 | 1920 | 2000

## Demand - AI
Demand Forecast for All-Island
2.4 The Combined All-Island Forecast
Figure 4.17 - Combined TER Forecast for the All-Island System
| Year | Historical (TWh) | Low (TWh) | Median (TWh) | High (TWh) | GCS22 Median (TWh)
| 2019 | 39.1
| 2020 | 38.9
| 2021 | 40.3
| 2022 |  | 41.65 | 41.69 | 41.71 | 42.5
| 2023 |  | 42.38 | 43.29 | 43.82 | 44.6
| 2024 |  | 43.1 | 45.1 | 46.84 | 46.6
| 2025 |  | 43.93 | 46.88 | 49.77 | 47.8
| 2026 |  | 44.75 | 48.74 | 52.36 | 49.5
| 2027 |  | 45.75 | 50.69 | 55.31 | 51
| 2028 |  | 46.57 | 52.07 | 57.53 | 52.6
| 2029 |  | 47.3 | 53.48 | 59.37 | 53.9
| 2030 |  | 48.07 | 54.9 | 61.05 | 55.2
| 2031 |  | 48.92 | 56.6 | 62.8 | 56.5
| 2032 |  | 49.8 | 58.38 | 64.67
Figure 4.18 - TER Peak for the Combined All-Island Forecast
| Year | Historic (MW) | Low (MW) | Med (MW) | High (MW) | GCS22 (MW)
| 2019 | 6900
| 2020 | 6983
| 2021 | 7120
| 2022 | 7017
| 2023 |  | 7070 | 7380 | 7660 | 7620
| 2024 |  | 7120 | 7590 | 7970 | 7900
| 2025 |  | 7190 | 7800 | 8270 | 8070
| 2026 |  | 7270 | 8020 | 8580 | 8160
| 2027 |  | 7410 | 8220 | 8950 | 8300
| 2028 |  | 7460 | 8350 | 9160 | 8430
| 2029 |  | 7510 | 8480 | 9340 | 8560
| 2030 |  | 7590 | 8640 | 9520 | 8670
| 2031 |  | 7670 | 8820 | 9730 | 8770
| 2032 |  | 7760 | 9030 | 9960

## Generation - Conventional IE
Conventional Generation - IE
3.2 Changes to Conventional Generation in Ireland
Table 5.3 -Assumptions for conventional plant changes in Ireland
| Plant | Units | Export Capacity (MW) | Modelled as closing by the end of: | Comment
| Aghada | AT1 | 90 | 2023 | IED Limited Life-time Derogation.
ESB has provided a closure notice for these units.
| Tarbert | TB1 | 54 | 2021 | SSE has previously provided a closure notice for this unit to close by the end of 2023.
TB1 has since been placed on outage until Dec 2023 so will be excluded from studies
|  | TB2 | 54 | 2021 | SSE has previously provided a closure notice for this unit to close by the end of 2023.
TB2 has since been placed on outage until Dec 2023 so will be excluded from studies
|  | TB3 | 241 | 2022 | SSE has previously provided a closure notice for this unit to close by the end of 2023.
TB2 has since been placed on outage until Dec 2023 so will be excluded from studies
|  | TB4 | 243 | 2021 | SSE has previously provided a closure notice for this unit to close by the end of 2023.
TB4 has since been placed on outage until Dec 2023 so will be excluded from studies
| Moneypoint | MP1 | 250 | 2024 | ESB have issued a closure notice for these units to close in October 2024. EirGrid notes that these units may be retained beyond this date for security of supply purposes. However, this is considered a mitigating measure and not part of the GCS core scenario.
|  | MP2 | 250 |  | MP2 is now running on Heavy Fuel Oil (HFO) with a capacity of 250 MW. The declared availability of MP1 and MP3 has declined recently and is now on average 250 MW.
|  | MP3 | 250
| Edenderry | ED1 | 118 | 2030 | The Bord na Móna plant ED1 was due to close at the end of 2023. Planning permission was recently awarded to keep this unit operating until 2030, running on 100% biomass from 2024.
|  | ED3 | 58 | N/A | Switching fuel by 2026 from Distillate Oil to Gas
|  | ED5 | 58 | N/A | Switching fuel by 2026 from Distillate Oil to Gas
Appendix 3 Generation Plant Information
Table A4-1 Registered Capacity of dispatchable generation and interconnectors in Ireland in 2023 (MW) DSU: Demand Side Unit; HFO: Heavy Fuel Oil; DO: Distillate Oil
|  | ID | Fuel Type | Technology Category | 2023 (MW) | Comment
| Aghada | AT1 | Gas/DO | Gas Turbine | 90 | To close before end of 2023
|  | AT2 | Gas/DO | Gas Turbine | 90
|  | AT4 | Gas/DO | Gas Turbine | 90
|  | AD2 | Gas/DO | Gas Turbine | 449
| All DSU | DSU | DSU | DSU | 639
| Ardnacrusha | AA1-4 | Hydro | Hydro | 86
| Dublin Bay | DB1 | Gas/DO | Gas Turbine | 415
| Dublin Waste | DW1 | Waste | Steam Turbine | 61
| Edenderry | ED1 | Milled peat/ Biomass | Steam Turbine | 118 | Planning Permission was granted to extend operation to 2030. Will run exclusively on biomass from Jan 2024
|  | ED3 | DO/Gas | Gas Turbine | 58 | Operating on gas from Oct 2025
|  | ED5 | DO/Gas | Gas Turbine | 58 | Operating on gas from Oct 2025
| Erne | ER1-4 | Hydro | Hydro | 65
| EWIC | EW1 |  | DC Interconnector | 500
| Great Island CCGT | GI4 | Gas/DO | Gas Turbine | 464
| Huntstown | HNC | Gas/DO | Gas Turbine | 337
|  | HN2 | Gas/DO | Gas Turbine | 408
| Indaver Waste | IW1 | Waste | Steam Turbine | 17
| Lee | LE1-4 | Hydro | Hydro | 27
| Liffey | LI1-4 | Hydro | Hydro | 38
| Moneypoint | MP1 | Coal/HFO | Steam Turbine | 250 | Modelled as not available from October 2024
|  | MP2 | HFO | Steam Turbine | 250 | Modelled as not available from October 2024
|  | MP3 | Coal/HFO | Steam Turbine | 250 | Modelled as not available from October 2024
| Poolbeg CC | PBA | Gas/DO | Gas Turbine | 234
|  | PBB |  | Gas Turbine | 234
| Rhode | RP1 | DO | Gas Turbine | 52
|  | RP2 | DO | Gas Turbine | 52
| Sealrock | SK3 | Gas/DO | Gas Turbine | 81
|  | SK4 | Gas/DO | Gas Turbine | 81
| Tarbert | TB1 | HFO | Steam Turbine | 54 | Unit has been placed on outage until Dec 2023. Scheduled to close thereafter.
|  | TB2 | HFO | Steam Turbine | 54
|  | TB3 | HFO | Steam Turbine | 241
|  | TB4 | HFO | Steam Turbine | 243
| Tawnaghmore | TP1 | DO | Gas Turbine | 52
|  | TP3 | DO | Gas Turbine | 52
| Turlough Hill | TH1 | Pumped storage | Storage | 292
| Tynagh | TYC | Gas/DO | Gas Turbine | 389
| Whitegate | WG1 | Gas/DO | Gas Turbine | 450
| Total Dispatchable including DSU |  |  |  | 7321

## Generation - Conventional NI
Conventional Generation - NI
3.3 Changes to Conventional Generation in Northern Ireland
Table 5.4 - Assumptions for Kilroot GT plant capacity
| Plant | Export Capacity (MW) | Modelling Assumption | Comment
| KGT1 | 29 | Unavailable in 2025 | Did not qualify for inclusion in T-4 2024/25 auction
| KGT2 | 29 | Unavailable in 2025 | Did not qualify for inclusion in T-4 2024/25 auction
| KGT3 | 42 | Unavailable in 2025 | Did not qualify for inclusion in T-4 2024/25 auction
| KGT4 | 42 | Unavailable in 2025 | Did not qualify for inclusion in T-4 2024/25 auction
Table 5.5 - Assumptions for plant changes in Northern Ireland
| Plant | Export Capacity (MW) | Modelled as closing by the end of: | Comment
| Kilroot ST1 | 130 | End of September 2023 | EPUKI, the owner of Kilroot, has provided a closure notice for this unit. Operation ceases 30th September 2023. The 238 MW is based on the HFO rating; however, the station has been declared unavailable for HFO operation for significant periods during 2021 and 2022. Due to Environmental Permit Compliance Restrictions, the unit is assumed to be 130 MW for modelling purposes.
| Kilroot ST2 | 130 | End of September 2024 | EPUKI has provided a closure notice for this unit. Operation ceases 30th September 2023. The 238 MW is based on the HFO rating; however, the station has been declared unavailable for HFO operation for significant periods during 2021 and 2022. Due to Environmental Permit Compliance Restrictions, the unit is assumed to be 130 MW for modelling purposes.
Appendix 3 Generation Plant Information
Table A4-4 Registered Capacity of dispatchable generation and interconnectors in Northern Ireland in 2023 (MW).
|  | ID | Fuel Type | Technology Category | 2023 (MW) | Comment
| Ballylumford | B31 | Gas/Heavy Fuel Oil | Gas Turbine | 246
|  | B32 | Gas/Heavy Fuel Oil | Gas Turbine | 246
|  | B10 | Gas/Heavy Fuel Oil | Gas Turbine | 101
|  | GT7(GT1) | Distillate Oil | Gas Turbine | 58
|  | GT8(GT2) | Distillate Oil | Gas Turbine | 58
| Kilroot | ST1 | Heavy Fuel Oil/Coal | Steam Turbine | 130 | Ceases operation in 2023
|  | ST2 | Heavy Fuel Oil/Coal | Steam Turbine | 130 | Ceases operation in 2023
|  | KGT1 | Distillate Oil | Gas Turbine | 29
|  | KGT2 | Distillate Oil | Gas Turbine | 29
|  | KGT3 | Distillate Oil | Gas Turbine | 42
|  | KGT4 | Distillate Oil | Gas Turbine | 42
| Coolkeeragh | GT8 | Distillate Oil | Gas Turbine | 53
|  | C30 | Gas/Distillate Oil | Gas Turbine | 408
| AGU | AGU | Distillate Oil | Gas Turbine | 79
| DSU | DSU | Various | DSU | 136
| Lisahally |  | Biomass |  | 18 | Not in Capacity Market, but assumed available for capacity requirement
| Contour Global | CGA / CGC | Gas | Gas Turbine | 12
| Moyle |  | DC Interconnector |  | 450
| Total Dispatchable plant: |  |  |  | 2267

## Generation - Non-Conventional
Non-Conventional Generation
3.4(a) North South Interconnector
Table 5.6 - Capacity reliance at present on the existing North South Interconnector
|  | North to South | South to North
| Capacity Reliance | 100 MW | 200 MW
3.4(c) Further Interconnection
Table 5.7 - Future Interconnection Projects
| Project | Description | Project Promoters Target Commissioning Year
| Celtic Interconnector | Interconnector between Ireland and France (with PCI status) | 2026
| Greenlink Interconnector | Project providing interconnection between Ireland and Wales | 2024
| LirIC | Interconnector between Northern Ireland and Scotland | 2028
| MARES Connect | Interconnector between Ireland and Wales | 2027
3.6 Modelling of Non-Conventional Generation in Adequacy Studies
Figure 5.7 - Impact of Solar Using Net Demand Methodology in Ireland in 2030
| 2030 Winter (MW) |  | 2030 Summer (MW)
| Demand | Demand Net Solar | Demand | Demand Net Solar
| 5244 | 5244 | 4557 | 4557
| 5156 | 5156 | 4483 | 4483
| 5046 | 5046 | 4426 | 4426
| 4964 | 4964 | 4369 | 4369
| 4920 | 4920 | 4322 | 4322
| 4863 | 4863 | 4293 | 4293
| 4847 | 4847 | 4288 | 4288
| 4831 | 4831 | 4278 | 4278
| 4821 | 4821 | 4284 | 4284
| 4806 | 4806 | 4312 | 4238
| 4850 | 4850 | 4311 | 4163
| 4906 | 4906 | 4338 | 3964
| 5060 | 5060 | 4464 | 3865
| 5261 | 5261 | 4599 | 3647
| 5624 | 5624 | 4860 | 3557
| 5887 | 5884 | 5124 | 3444
| 5914 | 5909 | 5275 | 3218
| 5899 | 5824 | 5295 | 2906
| 5996 | 5853 | 5332 | 2609
| 6030 | 5771 | 5374 | 2412
| 6009 | 5635 | 5365 | 2164
| 6011 | 5533 | 5390 | 2010
| 5986 | 5403 | 5364 | 1806
| 5962 | 5332 | 5329 | 1735
| 5963 | 5286 | 5348 | 1718
| 5968 | 5289 | 5391 | 1811
| 5897 | 5215 | 5348 | 1817
| 5845 | 5215 | 5323 | 1913
| 5849 | 5271 | 5305 | 2016
| 5823 | 5394 | 5293 | 2241
| 5858 | 5578 | 5298 | 2482
| 5910 | 5767 | 5303 | 2825
| 6019 | 6013 | 5276 | 3137
| 6262 | 6260 | 5316 | 3583
| 6415 | 6415 | 5363 | 4037
| 6453 | 6453 | 5364 | 4385
| 6410 | 6410 | 5294 | 4661
| 6315 | 6315 | 5215 | 4821
| 6247 | 6247 | 5103 | 4949
| 6161 | 6161 | 5064 | 4987
| 6062 | 6062 | 5060 | 5060
| 5977 | 5977 | 5089 | 5089
| 5839 | 5839 | 5083 | 5083
| 5712 | 5712 | 5077 | 5077
| 5592 | 5592 | 5078 | 5078
| 5502 | 5502 | 4961 | 4961
| 5548 | 5548 | 4850 | 4850
| 5388 | 5388 | 4690 | 4690
Figure 5.8 - Impact of Solar Using Net Demand Methodology in Northern Ireland in 2030
| 2030 Winter (MW) |  | 2030 Summer (MW)
| Demand | Demand Net Solar | Demand | Demand Net Solar
| 1151 | 1151 | 946 | 946
| 1119 | 1119 | 920 | 920
| 1125 | 1125 | 898 | 898
| 1109 | 1109 | 891 | 891
| 1102 | 1102 | 889 | 889
| 1086 | 1086 | 882 | 882
| 1084 | 1084 | 880 | 880
| 1079 | 1079 | 874 | 873
| 1083 | 1083 | 871 | 869
| 1086 | 1086 | 860 | 848
| 1098 | 1098 | 859 | 835
| 1122 | 1122 | 871 | 822
| 1193 | 1193 | 915 | 841
| 1278 | 1278 | 969 | 855
| 1421 | 1421 | 1045 | 891
| 1528 | 1528 | 1101 | 904
| 1585 | 1585 | 1151 | 910
| 1593 | 1587 | 1167 | 888
| 1609 | 1596 | 1194 | 877
| 1618 | 1588 | 1193 | 849
| 1615 | 1566 | 1183 | 813
| 1620 | 1553 | 1186 | 798
| 1613 | 1527 | 1181 | 776
| 1617 | 1516 | 1177 | 766
| 1621 | 1505 | 1179 | 763
| 1624 | 1509 | 1172 | 762
| 1596 | 1481 | 1154 | 753
| 1583 | 1487 | 1143 | 758
| 1590 | 1513 | 1135 | 767
| 1600 | 1549 | 1136 | 796
| 1616 | 1591 | 1144 | 832
| 1648 | 1636 | 1144 | 870
| 1732 | 1732 | 1161 | 925
| 1833 | 1833 | 1192 | 997
| 1870 | 1870 | 1208 | 1053
| 1838 | 1838 | 1204 | 1085
| 1784 | 1784 | 1178 | 1096
| 1742 | 1742 | 1156 | 1102
| 1699 | 1699 | 1135 | 1109
| 1673 | 1673 | 1119 | 1105
| 1642 | 1642 | 1117 | 1116
| 1613 | 1613 | 1114 | 1114
| 1561 | 1561 | 1100 | 1100
| 1505 | 1505 | 1094 | 1094
| 1434 | 1434 | 1105 | 1105
| 1352 | 1352 | 1084 | 1084
| 1285 | 1285 | 1034 | 1034
| 1222 | 1222 | 984 | 984
Figure 5.9 - Impact of Wind Using Net Demand Methodology in Ireland in 2030
| Winter Day Demand (MW) | Net Demand Low Wind (MW) | Net Demand High Wind (MW)
| 5244 | 4610 | 262
| 5156 | 4548 | 258
| 5046 | 4390 | 252
| 4964 | 4235 | 248
| 4920 | 4032 | 246
| 4863 | 3563 | 243
| 4847 | 3405 | 242
| 4831 | 3207 | 242
| 4821 | 2984 | 241
| 4806 | 2767 | 265
| 4850 | 2759 | 242
| 4906 | 2640 | 245
| 5060 | 2834 | 253
| 5261 | 3010 | 263
| 5624 | 3359 | 281
| 5887 | 3561 | 294
| 5914 | 3775 | 296
| 5899 | 3889 | 295
| 5996 | 4326 | 300
| 6030 | 4474 | 301
| 6009 | 4511 | 300
| 6011 | 4367 | 301
| 5986 | 4176 | 299
| 5962 | 4309 | 298
| 5963 | 4271 | 298
| 5968 | 4352 | 298
| 5897 | 4321 | 295
| 5845 | 4082 | 292
| 5849 | 4226 | 292
| 5823 | 4316 | 291
| 5858 | 4524 | 293
| 5910 | 4758 | 295
| 6019 | 4933 | 301
| 6262 | 5149 | 313
| 6415 | 5057 | 321
| 6453 | 5185 | 323
| 6410 | 5321 | 321
| 6315 | 5427 | 316
| 6247 | 5305 | 312
| 6161 | 5282 | 308
| 6062 | 5348 | 303
| 5977 | 5382 | 299
| 5839 | 5313 | 292
| 5712 | 5171 | 286
| 5592 | 5114 | 280
| 5502 | 5092 | 275
| 5548 | 5282 | 277
| 5388 | 5244 | 269
Figure 5.10 - Impact of Wind Using Net Demand Methodology in Northern Ireland in 2030
| Winter Day Demand (MW) | Net Demand Low Wind (MW) | Net Demand High Wind (MW)
| 1151 | 58 | 475
| 1119 | 56 | 430
| 1125 | 56 | 456
| 1109 | 55 | 509
| 1102 | 55 | 526
| 1086 | 54 | 538
| 1084 | 54 | 570
| 1079 | 54 | 597
| 1083 | 54 | 664
| 1086 | 54 | 722
| 1098 | 55 | 733
| 1122 | 56 | 747
| 1193 | 60 | 802
| 1278 | 133 | 880
| 1421 | 263 | 1025
| 1528 | 396 | 1085
| 1585 | 291 | 1184
| 1593 | 235 | 1305
| 1609 | 297 | 1423
| 1618 | 314 | 1437
| 1615 | 209 | 1489
| 1620 | 131 | 1555
| 1613 | 81 | 1566
| 1617 | 81 | 1565
| 1621 | 81 | 1566
| 1624 | 81 | 1561
| 1596 | 80 | 1535
| 1583 | 79 | 1529
| 1590 | 79 | 1531
| 1600 | 80 | 1563
| 1616 | 81 | 1594
| 1648 | 82 | 1643
| 1732 | 87 | 1732
| 1833 | 92 | 1833
| 1870 | 94 | 1870
| 1838 | 92 | 1812
| 1784 | 89 | 1706
| 1742 | 87 | 1596
| 1699 | 85 | 1445
| 1673 | 84 | 1261
| 1642 | 82 | 1124
| 1613 | 81 | 975
| 1561 | 78 | 808
| 1505 | 75 | 724
| 1434 | 72 | 621
| 1352 | 68 | 446
| 1285 | 64 | 425
| 1222 | 61 | 144
Table 5.8 - De-rating values used in AdCal studies
| Technology | De-rating value across 2022 - 2031
| Interconnectors | SEM <-> GB: 950 MWrated * 60% EMDF = 570 MW SEM <-> France: 700 MWrated * 60 %EMDF = 420 MW All Interconnectors are modelled with outage statistics as documented in Section 5.9
3.7(a) Demand Side Units (DSUs)
Table 5.9 - Ireland and Northern Ireland DSU Capacity (MW rated)
|  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| Ireland | 639 | 589 | 727 | 662 | 745 | 745 | 745 | 745 | 745 | 745
| Northern Ireland | 136 | 165 | 225 | 234 | 237 | 237 | 237 | 237 | 237 | 237
| Total | 775 | 754 | 952 | 896 | 982 | 982 | 982 | 982 | 982 | 982
3.7(b) Energy Storage
Table 5.10 - Total Storage Generation Capacity (MW rated) assumed in studies for Ireland and Northern Ireland
|  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| Ireland | 870 | 1020 | 1100 | 1140 | 1300 | 1300 | 1300 | 1300 | 1300 | 1300
| Northern Ireland | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
| Total | 1070 | 1220 | 1300 | 1340 | 1500 | 1500 | 1500 | 1500 | 1500 | 1500
Table 5.11 - Total Energy Storage Storage Capacity (MWh) assumed in studies for Ireland and Northern Ireland
|  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| Ireland | 2090 | 2390 | 2630 | 2720 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280
| Northern Ireland | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140
| Total | 2230 | 2530 | 2770 | 2860 | 3420 | 3420 | 3420 | 3420 | 3420 | 3420

## Generation - Renewable IE
Renewable Generation - IE
3.5(a) Wind Power in Ireland
Figure 5.3 - Assumed growth of renewable capacity in Ireland.
| Year | Onshore Wind (GW) | Offshore Wind (GW) | Solar (GW) | Renewable Waste (GW) | Biomass (GW) | Hydro (GW)
| 2023 | 4.6 | 0.03 | 0.79 | 0.04 | 0.15 | 0.24
| 2024 | 5.06 | 0.03 | 1.84 | 0.04 | 0.15 | 0.24
| 2025 | 5.11 | 0.03 | 2.44 | 0.04 | 0.15 | 0.24
| 2026 | 5.76 | 0.03 | 3.09 | 0.04 | 0.15 | 0.24
| 2027 | 6.4 | 0.03 | 3.74 | 0.04 | 0.15 | 0.24
| 2028 | 6.7 | 0.73 | 4.33 | 0.04 | 0.15 | 0.24
| 2029 | 7 | 2.87 | 4.91 | 0.04 | 0.15 | 0.24
| 2030 | 7 | 5 | 5.5 | 0.04 | 0.15 | 0.24
| 2031 | 7 | 7.14 | 6.09 | 0.04 | 0.15 | 0.24
| 2032 | 7 | 9.27 | 6.67 | 0.04 | 0.15 | 0.24
Figure 5.4 - The actual and normalised energy produced from wind power in Ireland over the last ten years.
| Year | Total Wind Generation (GWh) | Normalised Wind Generation (GWh) | Wind Capacity Factor (%) | Average Wind Capacity Factor (%)
| 2013 | 4642 | 4484 | 29% | 28%
| 2014 | 5116 | 5180 | 28% | 28%
| 2015 | 6537 | 5827 | 32% | 28%
| 2016 | 6115 | 6481 | 27% | 28%
| 2017 | 7229 | 7550 | 27% | 28%
| 2018 | 8685 | 8628 | 28% | 28%
| 2019 | 9532 | 9626 | 28% | 28%
| 2020 | 11138 | 10409 | 30% | 28%
| 2021 | 9527 | 10672 | 25% | 28%
| 2022 | 10895 | 10953 | 28% | 28%
Appendix 3 Generation Plant Information
Table A4-2 Partially/Non-Dispatchable plant in Ireland (MW)
| At year end: | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| Wind Onshore | 4595 | 5060 | 5110 | 5755 | 6400 | 6700 | 7000 | 7000 | 7000 | 7000
| Wind Offshore | 25 | 25 | 25 | 25 | 25 | 725 | 2865 | 5000 | 7135 | 9270
| Small Scale Hydro | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
| Biomass and Biogas | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| Biomass CHP | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
| Industrial | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
| Conventional CHP | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129
| Solar PV | 786 | 1838 | 2436 | 3089 | 3741 | 4327 | 4914 | 5500 | 6086 | 6672
| Total | 5624 | 7141 | 7789 | 9087 | 10384 | 11970 | 14997 | 17718 | 20439 | 23160
Table A4-3 All Renewable energy sources in Ireland (MW). We have assumed that the peat plant at Edenderry will be approximately 60% powered by biomass by 2023 and 100% biomass from 2024
| At year end: | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| All Wind | 4620 | 5085 | 5135 | 5780 | 6425 | 7425 | 9865 | 12000 | 14135 | 16270
| All Hydro | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242
| Biomass / LFG (including those units registered in the Capacity Market and Biomass CHP) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| Waste (Assume 50% Renewable) | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
| Peat Stations on Biomass | 77 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 0 | 0
| Solar | 786 | 1838 | 2436 | 3089 | 3741 | 4327 | 4914 | 5500 | 6086 | 6672
| Total RES | 5788 | 7346 | 7994 | 9292 | 10589 | 12175 | 15202 | 17923 | 20644 | 23365

## Generation - Renewable NI
Renewable Generation - NI
3.5(b) Wind Power in Northern Ireland
Figure 5.5 - The actual and normalised energy produced from wind power in Northern Ireland over the last ten years.
| Year | Total Wind Generation (GWh) | Normalised Wind Generation (GWh) | Wind Capacity Factor (%) | Average Wind Capacity Factor (%)
| 2013 | 1259 | 1255 | 23.18% | 23%
| 2014 | 1453 | 1386 | 24.22% | 23%
| 2015 | 1803 | 1499 | 27.81% | 23%
| 2016 | 1725 | 1715 | 23.26% | 23%
| 2017 | 2051 | 2123 | 22.34% | 23%
| 2018 | 2391 | 2460 | 22.46% | 23%
| 2019 | 2462 | 2584 | 22.02% | 23%
| 2020 | 2630 | 2584 | 23.52% | 23%
| 2021 | 2168 | 2660 | 18.84% | 23%
| 2022 | 2781 | 2735 | 23.51% | 23%
Figure 5.6 - Assumed growth of renewable capacity in Northern Ireland
| Year | Renewable Waste (GW) | Biomass (GW) | Solar PV (GW) | Onshore wind (GW) | Offshore wind (GW)
| 2022 | 0.03 | 0.04 | 0.24 | 1.33 | 0
| 2023 | 0.03 | 0.04 | 0.25 | 1.35 | 0
| 2024 | 0.03 | 0.04 | 0.28 | 1.44 | 0
| 2025 | 0.03 | 0.045 | 0.345 | 1.54 | 0
| 2026 | 0.03 | 0.05 | 0.401 | 1.61 | 0
| 2027 | 0.03 | 0.055 | 0.457 | 1.75 | 0
| 2028 | 0.03 | 0.06 | 0.509 | 1.99 | 0
| 2029 | 0.03 | 0.065 | 0.582 | 2.17 | 0
| 2030 | 0.03 | 0.07 | 0.617 | 2.46 | 0.5
| 2031 | 0.03 | 0.075 | 0.67733 | 2.74 | 0.5
| 2032 | 0.03 | 0.08 | 0.73133 | 3.03 | 0.5
Appendix 3 Generation Plant Information
Table A4-5 Partially/Non-Dispatchable plant in Northern Ireland (MW).
| At year end: | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| Large Scale Wind | 1169 | 1263 | 1356 | 1427 | 1571 | 1809 | 1993 | 2778 | 3063 | 3348
| Small Scale Wind | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
| Solar PV | 250 | 280 | 345 | 401 | 457 | 509 | 582 | 617 | 677 | 731
| Small Scale Biogas | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| Landfill Gas | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
| Small Scale Biomass | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Renewable CHP | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Other CHP | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Small Scale Hydro | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Waste-to-Energy | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
| Total | 1675 | 1799 | 1957 | 2084 | 2284 | 2574 | 2831 | 3651 | 3996 | 4335
Table A4-6 All Renewable energy sources in Northern Ireland (MW).
| At year end: | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| All Wind | 1349 | 1443 | 1536 | 1607 | 1751 | 1989 | 2173 | 2958 | 3243 | 3528
| Solar PV | 250 | 280 | 345 | 401 | 457 | 509 | 582 | 617 | 677 | 731
| All Biomass/Biogas/LFGas/WTE | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
| Renewable CHP | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Hydro | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Total RES | 1687 | 1811 | 1969 | 2096 | 2296 | 2586 | 2843 | 3663 | 4008 | 4347

## Generation - Auction Results
Generation Auction Results
3.1(a) SEM Capacity Market Auction Results
Figure 5.2 – All-Island derated successful new capacity in the T-4 2026-2027 Capacity Auction (non-risk adjusted)
| Auction | Gas Turbine (MWd) | Battery (MWd) | DSU (MWd) | Interconnecter (MWd)
| T-4 26/27 | 1124.36 | 105.25 | 68.88 | 220.25
Table 5.1 - Ireland assumptions for new conventional plant capacities in adequacy studies (rated MW). This risk adjusted view is based on plant delivering early, delivering late, or not delivering. For reference, the capacity successful in capacity auctions is also presented. Note all values are rounded to the nearest 10 MW.
| Ireland |  | 2024 | 2025 | 2026 | 2027 | 2028
| Gas Turbine | GCS2023 Risk Adjusted Capacity | 330 | 200 | 290 | 0 | 570
|  | Total Successful in Capacity Auctions | 230 | 1280 | 120 | 1270 | N/A
Table 5.2 - Northern Ireland assumptions for new conventional plant capacities in adequacy studies (rated MW). This risk adjusted view is based on plant delivering early, delivering late, or not delivering. For reference, the capacity successful in capacity auctions is also presented. Values are rounded to the nearest 10 MW.
| Northern Ireland |  | 2024 | 2025 | 2026 | 2027 | 2028
| Gas Turbine | GCS2023 Risk Adjusted Capacity | 720 | 0 | 0 | 0 | 0
|  | Total Successful in Capacity Auctions | 720 | 0 | 0 | 0 | 0
| Steam Turbine | GCS2023 Risk Adjusted Capacity | 0 | 0 | 0 | 310 | 0
|  | Total Successful in Capacity Auctions | 0 | 0 | 310 | 0 | 0
Appendix 3– Auction Results
Table A2-1 Capacity Market Auction Results
| Auction | Date | Awarded Capacity (De-Rated)
| 2018/2019 T-1 | 2017-12-15 | 7.774 GW
| 2019/2020 T-1 | 2018-12-13 | 8.266 GW
| 2020/2021 T-1 | 2019-11-26 | 7.606 GW
| 2021/2022 T-2 | 2019-12-05 | 7.512 GW
| 2022/2023 T-4 | 2019-03-28 | 7.412 GW
| 2023/2024 T-1 | 2021-10-21 | 1.121 GW
| 2024/2025 T-4 | 2020-04-27 | 7.322 GW
| 2022/2023 T-4 | 2021-01-21 | 6.618 GW
| 2024/2025 T-3 | 2022-01-20 | 1.471 GW
| 2025/2026 T-4 | 2022-03-24 | 6.484 GW
| 2026/2027 T-4* | 2023-03-23 | 7.204 GW
* Provisional Results
Table A2-2 - Units issued with Termination Notices since 2021 in addition to those identified in GCS 2021
| Plant | Technology Type | Auction | Contract Length | Awarded New Capacity Terminated (MW) | Termination Effective Date
| EnerNOC | DSU | 2022/2023 T-4 | 1 | 60.696 | 2021-05-08
| ESB | Gas Turbine | 2022/2023 T-4 | 10 | 192.36 | 2021-05-08
| ESB | Gas Turbine | 2022/2023 T-4 | 10 | 215.46 | 2021-01-11
| Statkraft | Wind | 2022/2023 T-4 | 1 | 44.5 | 2021-05-01
| Data and Power Hub | Gas Turbine | 2023/2024 T-4 | 10 | 105.328 | 2022-08-04
| Energia | Other Storage | 2023/2024 T-4 | 10 | 17.64 | 2021-12-07
| ESB | Gas Turbine | 2023/2024 T-4 | 1 | 11.49 | 2021-04-19
| EnerNOC | DSU | 2023/2024 T-4 | 1 | 12.147 | 2021-12-07
| ESB | Gas Turbine | 2024/2025 T-4 | 1 | 10.14 | 2021-04-19
| Statkraft | Gas Turbine | 2024/2025 T-4 | 10 | 45.1 | 2021-08-18
| Rhode Energy Storage | Other Storage | 2024/2025 T-3 | 1 | 14.25 | 2022-04-28
| Total |  |  |  | 729.111

## Generation - Availability
Generation Auction Results
3.1 Introduction
Figure 5.1 - Age breakdown of dispatchable plant on the All-Island system as of 2023
|  | Age | Capacity (MW)
| Thermal | < 10 years | 543
|  | 10 - 20 years | 3296
|  | 20 - 30 years | 1338
|  | 30 - 40 years | 869
|  | > 40 years | 1230
| Hydro | 8 - 59 years | 292
|  | 60 - 79 years | 130
|  | > 80 years | 86
3.8 Plant Availability
Table 5.12 – Summary of availability parameters used in the study
| Technology Category | Mean Forced Outage Probability (%) | Mean Scheduled Outage Rate (weeks)
| DSU | 35.6% | 14
| Gas Turbine | 9.1% | 3
| Hydro | 8.3% | 3
| Steam Turbine | 9.1% | 4
| Pumped Storage | 3.6% | 3
| System Wide | 9.1% | 3
| Interconnector | 4.5% | 2
Figure 5.11 - All-island average annual conventional generation capacity availability for the past 10 years (excluding DSU)
| Year | All Island Availability (%) | 2017 5-Year Average | 2022 5-Year Average
| 2011 | 86.7
| 2012 | 88.1
| 2013 | 88.9 | 88.68
| 2014 | 85.1
| 2015 | 89.5
| 2016 | 89.7
| 2017 | 90.2
| 2018 | 84.7 |  | 78.26
| 2019 | 79.8
| 2020 | 81.1
| 2021 | 71.3
| 2022 | 74.4
Figure 5.12 - Average annual conventional generation capacity Forced Outage Rates in Ireland for the past 10 years (excluding DSU)
| Year | Forced Outage Rate (IE) (%) | 5 Year Average 2014-2018 (%) | 5 Year Average 2017-2021 (%)
| 2011 | 7.5
| 2012 | 5.3
| 2013 | 5.7 | 5
| 2014 | 6.8
| 2015 | 2.9
| 2016 | 4.1
| 2017 | 5.5
| 2018 | 6.8 |  | 13.94
| 2019 | 10.3
| 2020 | 12.6
| 2021 | 21.9
| 2022 | 18.1
Figure 5.13 - Average annual conventional generation capacity Forced Outage Rates in Northern Ireland for the past 10 years (excluding DSU)
| Year | Forced Outage Rate (NI) (%) | 5 Year Average 2014-2018 (%) | 5 Year Average 2017-2021 (%)
| 2011 | 4.3
| 2012 | 9.8
| 2013 | 4.9 | 7.16
| 2014 | 9.6
| 2015 | 10.3
| 2016 | 4.6
| 2017 | 6.4
| 2018 | 9.9 |  | 11.38
| 2019 | 10.5
| 2020 | 9.7
| 2021 | 12.7
| 2022 | 14.1
Figure 5.14 - Ireland and Northern Ireland Conventional Generation Capacity Availability for the last 5 years (excluding DSU)
| Date | Ireland (%) | Northern Ireland (%)
| 2018-01-01 | 89.9 | 90.9
| 2018-02-01 | 89.6 | 91.4
| 2018-03-01 | 89 | 91.4
| 2018-04-01 | 88.4 | 90.9
| 2018-05-01 | 88 | 90.8
| 2018-06-01 | 87.7 | 89.5
| 2018-07-01 | 87.5 | 88.7
| 2018-08-01 | 87.4 | 87.8
| 2018-09-01 | 88 | 88.2
| 2018-10-01 | 86.9 | 87.8
| 2018-11-01 | 85.9 | 87
| 2018-12-01 | 84.1 | 86.6
| 2019-01-01 | 82.4 | 85.2
| 2019-02-01 | 81.6 | 84
| 2019-03-01 | 80.7 | 83
| 2019-04-01 | 80.2 | 82.2
| 2019-05-01 | 79.7 | 81
| 2019-06-01 | 79.2 | 80.8
| 2019-07-01 | 78.5 | 80.6
| 2019-08-01 | 77.6 | 80.1
| 2019-09-01 | 76.6 | 80.2
| 2019-10-01 | 77 | 80.7
| 2019-11-01 | 78.2 | 81
| 2019-12-01 | 79.4 | 81.1
| 2020-01-01 | 80.4 | 81.8
| 2020-02-01 | 80.9 | 82.2
| 2020-03-01 | 81.2 | 82.6
| 2020-04-01 | 81.5 | 83.7
| 2020-05-01 | 81.8 | 84.8
| 2020-06-01 | 82 | 85.7
| 2020-07-01 | 81.9 | 86.4
| 2020-08-01 | 81.9 | 86.1
| 2020-09-01 | 81.9 | 85.7
| 2020-10-01 | 81.7 | 83.9
| 2020-11-01 | 81.3 | 82.2
| 2020-12-01 | 80.7 | 82.6
| 2021-01-01 | 80.2 | 82.9
| 2021-02-01 | 79 | 82.8
| 2021-03-01 | 78.3 | 82.4
| 2021-04-01 | 77 | 82
| 2021-05-01 | 75 | 81.2
| 2021-06-01 | 73.6 | 79.7
| 2021-07-01 | 72.3 | 79
| 2021-08-01 | 71.4 | 79.9
| 2021-09-01 | 70 | 79
| 2021-10-01 | 69.4 | 79
| 2021-11-01 | 68.8 | 79.2
| 2021-12-01 | 69.4 | 78.3
| 2022-01-01 | 69.9 | 78
| 2022-02-01 | 71 | 78
| 2022-03-01 | 71.1 | 78.5
| 2022-04-01 | 71.6 | 77.8
| 2022-05-01 | 72 | 77
| 2022-06-01 | 72.4 | 77.2
| 2022-07-01 | 72.8 | 76.7
| 2022-08-01 | 73.3 | 75
| 2022-09-01 | 74.1 | 75
| 2022-10-01 | 74.1 | 75.1
| 2022-11-01 | 74.2 | 75.2
| 2022-12-01 | 74.1 | 75.3
| 2023-01-01 | 74.1 | 75.3
Figure 5.15 - All-Island Demand Side Unit Monthly Availability for 2022 Calendar year
|  | DSU MW Capacity (Rated) | DSU Monthly Availability (MW) | DSU Awarded Capacity (De-rated) (MW)
| 2022-01-01 | 731 | 162 | 471
| 2022-02-01 | 731 | 187 | 471
| 2022-03-01 | 731 | 178 | 471
| 2022-04-01 | 731 | 198 | 471
| 2022-05-01 | 731 | 197 | 471
| 2022-06-01 | 731 | 198 | 471
| 2022-07-01 | 731 | 157 | 471
| 2022-08-01 | 731 | 162 | 471
| 2022-09-01 | 731 | 189 | 471
| 2022-10-01 | 731 | 184 | 471
| 2022-11-01 | 731 | 184 | 471
| 2022-12-01 | 731 | 146 | 471

## Adequacy
Adequacy
4.1 Adequacy Results for Ireland
Table 6.1 - Results of adequacy studies for Ireland given in MW of surplus plant (+) or deficit (-) Figure 6.1 – Core scenario adequacy analysis for Ireland in terms of surplus (+) and deficit (-) of plant
| Core Scenarios | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| Low Demand | -580 | -350 | -900 | -670 | -430 | 10 | 40 | 40 | -80 | -120
| Median Demand | -750 | -610 | -1250 | -1130 | -920 | -550 | -560 | -630 | -840 | -950
| High Demand | -880 | -870 | -1590 | -1510 | -1440 | -1120 | -1200 | -1280 | -1480 | -1590
Sensitivities on Median Demand
| No NS Availability | -850 | -710 | -1350 | -1230 | -1020 | -650 | -660 | -730 | -940 | -1050
| SOEF v1.1 Low Emissions Scenario RES Trajectory | -730 | -560 | -1130 | -1030 | -800 | -410 | -460 | -530 | -740 | -860
| All new units delivering on time | -750 | -690 | -460 | -430 | 780 | 710 | 670 | 600 | 410 | 310
Table 6.2 - Loss of Load Expectation (LOLE) in hours for Ireland in the median scenario. Previous reported LOLE included operational requirements.
| Hours | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| LOLE Including demand and operational requirements (Hours) | 174 | 102 | 728 | 474 | 252 | 70 | 70 | 83 | 140 | 175
| LOLE Demand Only (Hours) | 52 | 29 | 303 | 188 | 52 | 11 | 12 | 15 | 32 | 46
Figure 6.2 - Ireland Adequacy Position with Mitigating Measures
4.4 Adequacy Results for Northern Ireland
Figure 6.3 - Adequacy results for Northern Ireland, in terms of surplus (+) or deficit (-) of plant (MW) Table 6.3 - Results of adequacy studies for Northern Ireland, given in ME of surplus plant (+) or deficit (-)
| Scenario | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| Low Demand | 10 | -40 | -170 | -50 | 510 | 520 | 530 | 550 | 560 | 560
| Median Demand | -30 | -110 | -240 | -150 | 400 | 400 | 390 | 400 | 380 | 350
| High Demand | -70 | -180 | -330 | -250 | 310 | 290 | 270 | 270 | 250 | 220
Sensitivities on Median Demand
| 1. No NS Reliance | -230 | -310 | -440 | -350 | 200 | 200 | 190 | 200 | 180 | 150
| 2. No NS Reliance & ARHL from 2027 | -230 | -310 | -440 | -350 | -360 | -360 | -370 | -360 | -380 | -420
| 3. ST Delivery from 2026 | -30 | -180 | -240 | 440 | 400 | 400 | 390 | 400 | 380 | 350
| 4. No ARHL | -30 | 270 | 130 | 220 | 400 | 400 | 390 | 400 | 380 | 350
Table 6.4 - Results of adequacy studies for Northern Ireland, given in hours of LOLE. Previous reported LOLE included operational requirements.
| LOLE | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| LOLE Including demand and operational requirements (Hours) | 6.5 | 15.7 | 50.4 | 21.5 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.3
| LOLE Demand Only (Hours) | 1.2 | 3.2 | 12.8 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0
4.5 Adequacy Results for the All-Island System
Figure 6.4 - Adequacy Results for the All-Island System Table 6.5 - Results of adequacy studies for the All-Island system (MW)
| Scenario | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| Low Demand | -470 | 470 | 890 | 900 | 900 | 800 | 770
| Median Demand | -1020 | -190 | 170 | 120 | 60 | -130 | -270
| High Demand | -1510 | -780 | -430 | -510 | -590 | -820 | -960
Table 6.6 - Loss of Load Expectation (LOLE) for All-Island System (hours)
| LOLE | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| LOLE Including demand and operational requirements (Hours) | 285 | 12 | 3 | 3 | 5 | 10 | 15
| LOLE Demand Only (Hours) | 17 | 0 | 0 | 0 | 0 | 0 | 0

## System Inputs - IE
Ireland Modelling Inputs
Ireland Demand
|  |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| GCS22 Median Transmission Peak Demand (MW) |  | 5740 | 5900 | 6070 | 6250 | 6380 | 6500 | 6600 | 6730 | 6880 | 7040
| Reserve Requirement (MW) |  | 375 | 375 | 375 | 375 | 525 | 525 | 525 | 525 | 525 | 525
| Transmission Outage Planning (MW) |  |  |  | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350
| Total (MW) |  | 6115 | 6275 | 6795 | 6975 | 7255 | 7375 | 7475 | 7605 | 7755 | 7915
Ireland Generation Portfolio Unit Capacities
The modelling of the system’s ability to meet the fluctuating demand is a complex function of combined probabilities of forced outage rates, optimisation of scheduled outage, annual run hour limitations and storage capacity and duration. As such, a simple comparison of the demand and total capacities here is not indicative of the adequacy position. The rated capacities and availabilities below are the inputs provided into that complex function.
|  |  | 2023: Rated Capacities (MW) | Forced Outage Rate | Scheduled Outage Duration (weeks)
|  | ID | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| Aghada | AT1 | 2023: 90 | 2.1% | 1
|  | AT2 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 9.1% | 3
|  | AT4 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 9.1% | 3
|  | AD2 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 9.1% | 3
| Ardnacrusha | AA1 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 8.3% | 3
|  | AA2 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 8.3% | 3
|  | AA3 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 8.3% | 3
|  | AA4 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 8.3% | 3
| Dublin Bay | DB1 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 9.1% | 3
| Dublin Waste | DW1 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 9.1% | 3
| Edenderry | ED1 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 |  |  | 9.1% | 3
|  | ED3 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 9.1% | 3
|  | ED5 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 9.1% | 3
| Erne | ER1 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8.3% | 3
|  | ER2 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 8.3% | 3
|  | ER3 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 8.3% | 3
|  | ER4 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 8.3% | 3
| Great Island CCGT | GI4 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 9.1% | 3
| Huntstown | HNC | 337 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 9.1% | 3
|  | HN2 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 9.1% | 3
| Indaver Waste | IW1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 9.1% | 3
| Lee | LE1 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 8.3% | 3
|  | LE2 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 8.3% | 3
|  | LE3 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8.3% | 3
| Liffey | LI1 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 8.3% | 3
|  | LI2 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 8.3% | 3
|  | LI3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 8.3% | 3
|  | LI4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 8.3% | 3
| Moneypoint | MP1 | 2023: 250; 2024: 250 | 20.7% | 3
|  | MP2 | 2023: 250; 2024: 250 | 39.2% | 6
|  | MP3 | 2023: 250; 2024: 250 | 38% | 4
| Poolbeg CC | PBA | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 9.1% | 3
|  | PBB | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 9.1% | 3
| Rhode | RP1 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 9.1% | 3
|  | RP2 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 9.1% | 3
| Sealrock | SK3 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 9.1% | 3
|  | SK4 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 9.1% | 3
| Tawnaghmore | TP1 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 9.1% | 3
|  | TP3 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 9.1% | 3
| Tynagh | TYC | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 9.1% | 3
| Whitegate | WG1 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 9.1% | 3
| Turlough Hill | TH1 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 3.6% | 3
|  | TH2 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 3.6% | 3
|  | TH3 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 3.6% | 3
|  | TH4 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 3.6% | 3
| Industrial | INDU | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 91.7% | 0
| Small Scale Hydro | SSH | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 76.5% | 0
| Conventional CHP | CHP | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 37.45% | 0
| Landfill Gas | LFG | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 66.5% | 0
| CHP_Bio | CHP Bio | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 20% | 0
| Batteries[1] | Batteries | 580 | 730 | 810 | 850 | 1010 | 1010 | 1010 | 1010 | 1010 | 1010 | 9.1% | 3
| DSU[2] | DSU | 639 | 589 | 727 | 662 | 745 | 745 | 745 | 745 | 745 | 745 | 35.6% | 14
| Gas Turbine Auction Results |  |  | 330 | 530 | 820 | 820 | 1390 | 1390 | 1390 | 1390 | 1390 | 9.1% | 3
| GB to IE Interconnection[3] |  | 300[3] | 300[3] | 300[3] | 300[3] | 300[3] | 300[3] | 300[3] | 300[3] | 300[3] | 300[3] | 4.5% | 2
| FR to IE Interconnection[3] | [5 empty] | 420[3] | 420[3] | 420[3] | 420[3] | 420[3] | 420[3] | 4.5% | 2
[1] The contribution to system adequacy of battery storage is restricted by the size and duration.
[2] Circa 80% of the DSU capacity noted here has limitations on how many hours per day it can be utilised, restricting the duration of which this capacity can be delivered, and thus it’s ability to meet demand and contribute to adequacy. The average run hour limitation of these units is 2.3 hours per day.
[3] Interconnector rated capacities incorporates 60% External Market Derating Factor
Ireland Generation Portfolio Wind and Solar Capacities
Installed Capacity (MW)
| Source |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| Wind |  | 4620 | 5085 | 5135 | 5780 | 6425 | 7425 | 9865 | 12000 | 14135 | 16270
| Solar |  | 786 | 1838 | 2436 | 3089 | 3741 | 4327 | 4914 | 5500 | 6086 | 6672
Ireland Generation Portfolio Capacity Credits
Capacity Credit (MW)
| Source |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| NI Reliance |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100

## System Inputs - NI
Northern Ireland Modelling Inputs
Northern Ireland Demand
|  |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| GCS22 Median Transmission Peak Demand (MW) |  | 1560 | 1600 | 1640 | 1680 | 1750 | 1780 | 1800 | 1830 | 1850 | 1900
| Reserve Requirement (MW) |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
| Total (MW) |  | 1760 | 1800 | 1840 | 1880 | 1950 | 1980 | 2000 | 2030 | 2050 | 2100
Northern Ireland Generation Portfolio Unit Capacities
The modelling of the system’s ability to meet the fluctuating demand is a complex function of combined probabilities of forced outage rates, optimisation of scheduled outage, annual run hour limitations and storage capacity and duration. As such, a simple comparison of the demand and total capacities here is not indicative of the adequacy position. The rated capacities and availabilities below are the inputs provided into that complex function.
|  |  | 2023: Rated Capacities (MW) | Forced Outage Rate | Scheduled Outage Duration (weeks)
|  | ID | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| Ballylumford | B31 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 9.1% | 3
|  | B32 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 9.1% | 3
|  | B10 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 9.1% | 3
|  | GT7(GT1) | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 9.1% | 3
|  | GT8(GT2) | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 9.1% | 3
| Kilroot | ST1 | 2023: 130 | 20.8% | 4
|  | ST2 | 2023: 130 | 18.3% | 7
|  | KGT1 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 9.1% | 3
|  | KGT2 | 29 | 29 |  | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 9.1% | 3
|  | KGT3 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 9.1% | 3
|  | KGT4 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 9.1% | 3
| Coolkeeragh | GT8 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 9.1% | 3
|  | C30 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 9.1% | 3
| AGU | AGU | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 9.1% | 3
| Lisahally | Lisahally | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 9.1% | 4
| Contour Global | CGA / CGC | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 9.1% | 3
| CHP | NI_CHP | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 39% | 0
| Biogass | NI_BIOGAS | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 56% | 0
| Biomass | NI_BIOMASS | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 70.3% | 0
| Renewable CHP | NI_CHP_RES | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 39.5% | 0
| Hydro | NI_SSH | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 67% | 0
| Landfill Gas | NI_LFG | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 46.1% | 0
| Diesel | NI_DIESEL | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 87.5% | 0
| Batteries[1] | Batteries | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 9.1% | 3
| DSU[2] | DSU | 136 | 165 | 225 | 234 | 237 | 237 | 237 | 237 | 237 | 237 | 35.6% | 14
| Gas Turbine Auction Results |  |  | 720[3] | 720[3] | 720[3] | 720 | 720 | 720 | 720 | 720 | 720 | 9.1% | 3
| Steam Turbine Auction Results | [5 empty] | 310 | 310 | 310 | 310 | 310 | 310 | 9.1% | 3
| GB to NI Interconnection[4] |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 4.5% | 2
[1] The contribution to system adequacy of battery storage is restricted by the size and duration.
[2] Circa 80% of the DSU capacity noted here has limitations on how many hours per day it can be utilised, restricting the duration of which this capacity can be delivered, and thus it’s ability to meet demand and contribute to adequacy.
[3] Some of this capacity has annual run hour limitations. This has been represented through modelling by restricting the number of hours of running available to a unit per year. For example a unit with a 1,500 Annual run hour limit is forced to be unavailable for 7,260 hours per year. Restricting the availability of this capacity reduces the system’s ability to meet demand.
[4] Interconnector rated capacities incorporates 60% External Market Derating Factor
Northern Ireland Generation Portfolio Wind and Solar Capacities
Installed Capacity (MW)
| Source |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| Wind |  | 1349 | 1443 | 1536 | 1607 | 1751 | 1989 | 2173 | 2958 | 3243 | 3528
| Solar |  | 250 | 280 | 345 | 401 | 457 | 509 | 582 | 617 | 677 | 731
Northern Ireland Generation Portfolio RES Capacity Credits
Capacity Credit (MW)
| Source |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| IE Reliance |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200