## NI WIND QUARTERLY REPORT AUGUST 2006

# Strategic Review

##### Overview

In December 2004, we started to advise market players that we were unable to accept any more unconstrained capacity of wind farms in the North West region of our network.  The issue was a backbone system constraint (see below).  Since then we have managed to negotiate an improved operation of emergency network protection at Coolkeeragh Power station. This scheme operates after a defined very severe network event.  We are now able to allow a further circa 75MW of unconstrained capacity to be connected.  In 2006, network developments in the region will allow a further 50MW.  These figures are average and this report shows how they vary with location of connection.

Later in the Report we indicate that we believe a low level of summer constraint should be acceptable to wind farm power station operators. This should allow reasonable progress in connections to be made until network developments are completed in 2007.

### Information on Wind Penetration

NIE updates this statement on a regular basis.  This allows developers to understand the position.   For each issue (see below) we update the installed, committed etc columns and we note the progress on strategic issues.

# Process and General Issues which Limit Wind Power Penetration

There are a number of issues which limit the amount of wind power that NIE can safely accept. The significant issues are:

- Variability and energy services uncertainty

- Technical uncertainty (voltage management, fault ride through, reserve and so on)

- Local network issues

At present, NIE’s network has a total of 12 connected wind farms with a total installed capacity of 120.1MW. We have connected a new CCGT station in the NW, the total capacity of which is circa 472MW (Coolkeeragh).  Other enquiries for wind powered stations amount to some 1700MW (incl off-shore).  Most of this new generation is expected in the north or west of our area of supply, away from electrically strong networks.  We have also been asked to connect to NIE’s network, generation just inside RoI.

Clearly, taken together this amount of wind is likely to create unmanageable variability.  Nor are we clear that with reduced system inertia caused by certain types of wind farm power stations, the technical issues could be managed, so some level of constraint is likely to be imposed even before we consider local network capacity issues.  We held a meeting in May 2004 with our Regulator and interested parties to discuss the most effective and equitable rules to be applied.

As a result we now apply a rule that only projects which have obtained Planning Permission can be offered a Connection Agreement.  This is to prevent unsuccessful projects retaining capacity at nodes. This concept seems to be supported by the industry and accepted by our Regulator.

To understand the main issues we have constructed a summer minimum case for the year 2006.  The existing wind farms and projects under offer have been included.  Summer minimum is the most arduous condition for two reasons:

- Circuit ratings are lower in summer due to higher ambient temperature,

- The load present at local nodes is much less on summer evenings, therefore the circuits have a higher export flow.

33kV Capacity Review

The following table shows the level of interest from developers on the basis of requested capacity at each 33kV node.

| BSP | Existing Wind Generation (MW) | Committed Wind Generation Projects (MW) | Additional Enquiries (MW) | Total Potential Generation (MW) |
| --- | --- | --- | --- | --- |
| Belfast Ballymena Coleraine Coolkeeragh Dungannon Eden Enniskillen Larne Limavady Lisaghmore Omagh Strabane ### TOTALS | 0.0 6.0 5.0 0.0 0.0 0.0 35.4 5.0 26.0 0.0 37.7 5.0 120.1 | 11.5 11.7 11.7 23.1 58.0 | 45.00 1.80 60.00 81.00 46.00 14.00 100.00 19.25 10.30 13.00 150.00 121.80 662.15 | 45.00 7.80 65.00 81.00 46.00 14.00 135.40 35.75 48.00 13.00 199.40 149.90 840.25 |

The above generation is reflected into the 110kV system and there are some connections which are requested at this level as follows: -

| BSP | Total Potential Generation @ 33kV (MW) | Enquiries requiring connection @ 110kV (MW) | Total Potential Wind Generation (MW) | Comments |
| --- | --- | --- | --- | --- |
| Belfast Ballymena Coleraine Coolkeeragh Dungannon Eden Enniskillen Larne Limavady Lisaghmore Newry Omagh Strabane TOTALS | 45.00 7.80 65.00 81.00 46.00 14.00 135.40 35.75 47.00 13.00 0.00 199.40 149.90 839.25 | 200.00 60.00 85.00 200.00 231.00 75.00 851.00 | 45.00 7.80 265.00 81.00 46.00 14.00 195.40 35.75 132.00 13.00 200.00 430.40 224.90 1690.25 |  |

Backbone Network Issues

Coolkeeragh is a generation saturated node, we have negotiated that the CCGT generator is returned to an output of 160MW over a period of 100 seconds, on the worst case circuit outage – Coolkeeragh-Magherafelt 275kV double circuit.  Since temporary overloading of the network over this period would be acceptable, the network connection capacity has been calculated with the CCGT at 160MW.

In assessing wind potential we have assumed that the OCGT (GT8) at Coolkeeragh will not be operating at summer minimum along with both elements of the CCGT.

There is more scope to accept wind power higher up the loading curve as local loads will reduce export.

The following Table 1 shows the results of transmission network studies, which we have carried out to date. These results are based on the existing network and reflect the impact of approved network reinforcements which will be completed in 2007.

###### Table 1: Existing available nodal capacity

| Bulk Supply Point | Availability of unconstrained wind generation | Constraint |
| --- | --- | --- |
| Strabane | 124MW / 28MW* | Omagh-Dunagnnon A 110kV Thermal / BSP Transformers* |
| Omagh | 104MW / 28MW | Omagh-Dungannon A 110kV Thermal / BSP Transformers |
| Enniskillen | 75MW / 73MW | Enniskillen-Omagh A or B 110kV Thermal / BSP Transformers |
| Coolkeeragh | 125MW / 112MW | Coolkeragh-Magherafelt 275kV A or B Thermal / BSP Transformers |
| Limavady | 53MW / 15MW | Coolkeeragh-Limavady 110kV Thermal / BSP Transformers |
| Coleraine/ Loguestown | 90MW / 66MW | Coolkeeragh-Limavady 110kV Thermal / BSP Transformers |
| Dungannon | 92MW | Dungannon-Drumnakelly A 110kV Thermal |

* The first value is caused by the first constraint and the second value is caused by the second constraint. Please note that it should be possible to remove the second constraint with the use of automatic local control schemes.

Our studies are based on Summer 2006.

Table 2 shows the impact of an approved 275/110kV substation near Coalisland which is planned for completion by Summer 2008.

###### Table 2: Available capacity following completion of Coalisland Main 275/110kV S/Stn

| BSP | Availability of unconstrained wind generation | Constraint |
| --- | --- | --- |
| Strabane | 120MW / 28MW | Omagh-Dunagnnon A 110kV Thermal / BSP Transformers |
| Omagh | 101MW / 28MW | Omagh-Dunagnnon A 110kV Thermal / BSP Transformers |
| Enniskillen | 74MW / 73MW | Enniskillen-Omagh A or B 110kV Thermal / BSP Transformers |
| Coolkeeragh | 132MW / 112MW | Coolkeragh-Magherafelt 275kV A or B Thermal / BSP Transformers |
| Limavady | 53MW / 15MW | Coolkeeragh-Limavady 110kV Thermal / BSP Transformers |
| Coleraine/ Loguestown | 95MW / 66MW | Coolkeeragh-Limavady 110kV Thermal / BSP Transformers |
| Dungannon | 127MW / 118MW | Dungannon-Coalisland 110kV Thermal / BSP Transformers |

The nodes around Coolkeeragh, Strabane, Omagh, Limavady, Coleraine and Loguestown have linked network capacity and increasing generation at one node affects the connection capacity at all nodes. Table 3 shows approximately the effect on capacity of installing generation at any node.

# Table 3: Participation factor matrix

| New Gen / Effect on Capacity | #### Nodes |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Cole | Ennisk | Omagh | Strabane | Lima | Coolk | Dungannon |
| Coleraine |  | -2.33 | -2.33 | -1.51 | -1.05 | -1.29 | -0.54 |
| Enniskillen | -0.37 |  | -0.92 | -0.60 | -0.41 | -0.51 | -0.89 |
| Omagh | -0.37 | -0.92 |  | -0.59 | -0.41 | -0.50 | -0.88 |
| Strabane | -0.56 | -1.38 | -1.38 |  | -0.62 | -0.76 | -0.74 |
| Limavady | -0.81 | -2.02 | -2.02 | -1.31 |  | -1.11 | -0.58 |
| Coolkeeragh | -0.65 | -1.61 | -1.61 | -1.05 | -0.72 |  | -0.67 |
| Dungannon | -0.16 | -0.39 | -0.39 | -0.25 | -0.17 | -0.21 |  |

The value of each cell represents the connection capacity reduction at the node identified by the column heading for each MW connected at the node identified in column 1.

The participation factors shown above are calculated for the loss of the Coolkeeragh-Magherafelt 275kV double circuit.  This analysis is for guidance purposes only and the effect of each connection application on the network capacity will be individually assessed.

Example

The Participation Factor Matrix shows the interaction between network nodes.

The connection of 1MW of generation at Strabane results in a corresponding reduction of unconstrained generation at each of the following nodes in the table.

|  | Cole | Ennisk | Omagh | Strabane | Lima | Coolk | D’gannon |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Strabane | -0.56 | -1.38 | -1.38 |  | -0.62 | -0.76 | -0.74 |

Constraint

We carried out studies in Summer 2005, which support a view that if the output of wind farms were constrained to 93% of installed capacity during summer periods, this would not materially affect their commercial performance.  This addressed an inaccuracy in our Summer 2004 report caused by wind farm transducers malfunctioning.  In our next Quarterly Report we will attempt to indicate the impact which this would have on network issues.

Diversity

The same report demonstrates that wind farm power stations in Northern Ireland have highly correlated outputs when long periods e.g. 1 day and above are considered, but that there is diversity of output when viewed over short time periods…say one hour or less.

Study progress

We have sought permission from wind farm operators to carry out more studies in support of our constraint and diversity conclusions above and we will shortly report on that work.

Grid Code Changes

We have received consensus on our Grid Code changes for wind farm power stations and anticipate Regulatory approval before the end of February 2006. There remains some unfinished work around sub-synchronous harmonics, islanding protection and inertia.  In the mean time, in conjunction with the system operator (SONI) we have been considering the other sections of the Grid Code, some of which have terms or conditions not suited to wind farms, e.g. the Scheduling and Dispatch Code.  We intend to include these amendments in the Single Electricity Market change for 2007 and will consult on any changes needed.  We do not envisage these changes to require the same degree of manufacturer participation as those related to plant capability.

Compliance with Grid Code

We have recently developed a document that sets out how compliance is to be demonstrated for Wind Farm Power Stations.  We realise that all parties will be in a learning position and that mutual good will is required in the early stages.

Connection Arrangements

In anticipation of a day when constraint on network or variability management grounds will be a real issue, we have been considering the process of agreeing connection of variable generation sources.  We intend to propose to our Regulator that relevant parties are consulted on this.  In this way, we hope to establish transparent arrangements that the market players agree are equitable.  In the meantime we have prepared a generic form of a connection agreement for wind farm power stations.