## Front Page
All Island Resource Adequacy Assessment 2026-2035 Data Workbook
Purpose: To publicly share the data used throughout the All-Island Resource Adequacy Assessment 2026-2035. For any questions on this data, please contact info@EirGrid.com or info@SONI.ltd.uk, referencing the All-Island Resource Adequacy Assessment 2026-2035 in the subject line.
Disclaimer: EirGrid Plc and SONI Ltd have followed accepted industry practice in the collection and analysis of data available. While all reasonable care has been taken in the preparation of this data, EirGrid and SONI are not responsible for any loss that may be attributed to the use of this information. Prior to taking business decisions, interested parties are advised to seek separate and independent opinion in relation to the matters covered by this report and should not rely solely upon data and information contained herein. Information in this document does not amount to a recommendation in respect of any possible investment. This document does not purport to contain all the information that a prospective investor or participant in the Single Electricity Market (SEM) may need.
Version History:
| Version | Description | Date
| 1 | Initial Publication | February 2026
Contents (In order shown in report):
| Location in Report | Description | Link
| Table 4.1 | Average annual growth rates for macroeconomic parameters, values used for median demand as advised by the ESRI | Demand IE
| Table 4.2 | Forecasted data centre and new technology load demand by 2035. 2024 demand 959 MVA | Demand IE
| Figure 4.1 | Ireland demand expected from assumed build out of data centres and new technology loads | Demand IE
| Table 4.3 | 2030 EV & HP projections from SEAI's WEM Scenario in Median Scenario versus Climate Action Plan Targets 2024 | Demand IE
| Table 4.4 | Low, median and high Total Electricity Requirement key assumption differences by 2030 | Demand IE
| Figure 4.2 | Electric vehicle electrical energy demand - median scenario | Demand IE
| Figure 4.2 | Heat pump electrical energy demand - median scenario | Demand IE
| Figure 4.3 | Historic recorded and temperature corrected peak demand | Demand IE
| Figure 4.4 | Impact of demand flexibility on 2030 peak day (median scenario) | Demand IE
| Figure 4.5 | Impact of demand flexibility in median scenario across the study period | Demand IE
| Figure 4.6 | Total Electricity Requirement for Ireland | Demand IE
| Table 4.5 | Low, median and high Total Electricity Requirement key assumption differences by 2030 | Demand IE
| Figure 4.7 | Ireland median demand Total Electricity Requirement sectoral breakdown | Demand IE
| Figure 4.8 | Sectoral contribution to Ireland's Median TER in 2026 & 2035 | Demand IE
| Figure 4.9 | Sectoral contribution to Ireland's peak demand in 2026 & 2035 | Demand IE
| Figure 4.10 | Transmission peak forecast for Ireland | Demand IE
| Figure 4.11 | Forecast hourly demand shape in Ireland | Demand IE
| Figure 4.12 | Electric vehicle charging profiles | Demand IE
| Figure 4.13 | Northern Ireland TER expected from data centres across demand scenarios | Demand NI
| Table 4.6 | Number of electric vehicle and heat pump installations included in the low, median, and high demand forecast | Demand NI
| Table 4.7 | Low, median and high Total Electricity Requirement key assumption differences for Northern Ireland | Demand NI
| Figure 4.14 | Northern Ireland total electricity requirement (TER) forecast | Demand NI
| Figure 4.15 | Northern Ireland median total electricity requirement (TER) forecast components | Demand NI
| Figure 4.16 | Northern Ireland's total electricity requirement (TER) breakdown in 2026 and 2035 | Demand NI
| Figure 4.17 | Northern Ireland's total electricity requirement (TER) peak demand breakdown in 2026 and 2035 | Demand NI
| Figure 4.18 | ACS Transmission Peak forecasts for Northern Ireland | Demand NI
| Figure 4.19 | The impact of demand flexibility on 2030 peak day for Northern Ireland (median scenario) | Demand NI
| Figure 4.20 | Impact of demand flexibility in median scenario across the study period for Northern Ireland | Demand NI
| Figure 4.21 | Historical and forecast hourly demand shape in Northern Ireland | Demand NI
| Figure 4.22 | Combined TER forecast for all-island system | Demand AI
| Figure 4.23 | TER peak for the combined all-island forecast | Demand AI
| Figure 5.1 | Age breakdown of dispatchable conventional and hydro generation resources for the All-Island system operational from the start of 2026 | Generation - All Island
| Table 5.5 | North South Net Transfer Capacity | Generation - All Island
| Table 5.6 | HVDC Net Transfer Capacity (MW) assumptions for Northern Ireland/Ireland connection. Loss factors derived from Transmission Loss Adjustment Factors (TLAFs) for 2024-2025. The loss factor for Celtic is an anticipated loss factor based on engineering judgement of the EirGrid Interconnection team. | Generation - All Island
| Table 5.7 | Further interconnection projects | Generation - All Island
| Table 5.1 | Assumptions for conventional plant changes in Ireland | Generation - Conventional IE
| Table 5.2 | Ireland assumptions for new conventional plant capacities in adequacy studies (rated MW) | Generation - Conventional IE
| Table 5.3 | Capacity (MW) assumed to be subject to run hour limits in Ireland | Generation - Conventional IE
| Table 5.4 | Capacity (MW) assumed to be subject to run hour limits in Northern Ireland | Generation - Conventional NI
| Table 5.8 | Climate Action Plan renewable targets in Ireland | Generation - Renewable IE
| Figure 5.2 | Assumed growth of variable generation capacity in Ireland | Generation - Renewable IE
| Figure 5.3 | Assumed growth of renewable capacity in Northern Ireland | Generation - Renewable NI
| Table 5.9 | Ireland energy storage capacity (MW) rounded to the nearest 10 MW | Generation - Non-Conventional
| Table 5.10 | Ireland energy storage (MWh) rounded to the nearest 10 MWh | Generation - Non-Conventional
| Table 5.11 | Northern Ireland energy storage capacity (MW) rounded to the nearest 10 MW | Generation - Non-Conventional
| Table 5.12 | Northern Ireland energy storage (MWh) rounded to the nearest 10 MWh | Generation - Non-Conventional
| Table 5.13 | Ireland DSU capacity (MW) rounded to the nearest 10 MW | Generation - Non-Conventional
| Table 5.14 | Ireland DSU run hour restriction (hours) | Generation - Non-Conventional
| Table 5.15 | Northern Ireland DSU capacity (MW) rounded to the nearest 10 MW | Generation - Non-Conventional
| Table 5.16 | Northern Ireland DSU run hour restriction (hours) | Generation - Non-Conventional
| Table 5.17 | Northern Ireland AGU capacity (MW) | Generation - Non-Conventional
| Table 5.18 | Summary of technology class availability statistics | Generation - Availability
| Figure 5.4 | All-island average annual generation capacity availability for the past 10 years (excluding DSU) | Generation - Availability
| Figure 5.5 | Average annual conventional generation capacity forced and scheduled outage rates in Ireland for the past 10 years | Generation - Availability
| Figure 5.6 | Average annual conventional generation capacity forced and scheduled outage rates in Northern Ireland for the past 10 years | Generation - Availability
| Figure 5.7 | Ireland and Northern Ireland conventional generation capacity availability across the last 10 years | Generation - Availability
| Figure 5.8 | All-Island demand side unit monthly availability for 2022 to 2025 calendar years | Generation - Availability
| Table 6.1 | LOLE Reliability Standards | Adequacy
| Figure 6.2 | Base and Secure Loss of Load Expectation Results for Ireland | Adequacy
| Table 6.2 | LOLE and EENS Base results for Ireland (includes reserves) | Adequacy
| Table 6.3 | LOLE and EENS Base Demand Only results for Ireland (excludes reserves) | Adequacy
| Table 6.4 | Average LOLE of the 3 weather scenarios used in the surplus/deficit calculation for Ireland (includes reserves) | Adequacy
| Figure 6.3 | MW Base results for Ireland in terms of surplus (+) and deficit (-) of perfect plant | Adequacy
| Table 6.5 | LOLE and EENS Secure results for Ireland (includes reserves) | Adequacy
| Figure 6.4 | Secure surplus/deficit results for Ireland in terms of surplus (+) and deficit (-) of perfect plant | Adequacy
| Figure 6.5 | Sensitivity analysis for Ireland | Adequacy
| Table 6.6 | Low RES renewable trajectory (MW) | Adequacy
| Table 6.7 | High RES renewable trajectory (MW) | Adequacy
| Table 6.8 | Ireland high storage additional capacity | Adequacy
| Figure 6.6 | Ireland adequacy position with mitigating measures | Adequacy
| Figure 6.7 | Base and Secure Loss of Load expectation results for Northern Ireland | Adequacy
| Table 6.9 | LOLE and EENS Base results for Northern Ireland (includes reserves) | Adequacy
| Table 6.10 | LOLE and EENS base demand only results for Northern Ireland (excludes reserves) | Adequacy
| Table 6.11 | Average LOLE of the 3 weather scenarios used in the surplus/deficit calculation for Northern Ireland (includes reserves) | Adequacy
| Figure 6.8 | MW base results for Northern Ireland in terms of surplus (+) and deficit (-) of perfect plant | Adequacy
| Table 6.12 | LOLE and EENS Secure results for Northern Ireland (includes reserves) | Adequacy
| Figure 6.9 | MW secure results for Northern Ireland in terms of surplus (+) and deficit (-) of perfect plant | Adequacy
| Figure 6.10 | Sensitivity analysis for Northern Ireland | Adequacy
| Table 6.13 | Northern Ireland low renewable trajectory (MW) | Adequacy
| Table 6.14 | Northern Ireland high renewable trajectory (MW) | Adequacy
| Table 6.15 | Northern Ireland high storage additional capacity | Adequacy
| Table 6.16 | Base results for the All-Island system | Adequacy
| Table 6.17 | Secure results for the All-Island system | Adequacy
| Figure 6.11 | MW results for the All-Island in terms of surplus (+) and deficit (-) of perfect plant | Adequacy
| Table A1.1 | EVA considerations | Appendix 1
| Table A1.2 | Economic Viability Assessment (EVA) summary of scenarios | Appendix 1
| Figure A1.2 | Economic Viability Assessment (EVA) rated capacity changes compared to the central adequacy scenario | Appendix 1
| Table A2.1 | Demand forecast for the median scenario in calendar year format for Ireland and Northern Ireland | Appendix 2
| Table A2.2 | Demand forecast for the low scenario in calendar year format for Ireland and Northern Ireland | Appendix 2
| Table A2.3 | Demand forecast for the high scenario in calendar year format for Ireland and Northern Ireland | Appendix 2
| Table A3.1 | Registered capacity of dispatchable generation and interconnectors in Ireland in 2026 (MW) | Appendix 3
| Table A3.2 | Partially/non-dispatchable plant in Ireland (MW) | Appendix 3
| Table A3.3 | Registered capacity of dispatchable generation and interconnectors in Northern Ireland in 2026 (MW) | Appendix 3
| Table A3.4 | Partially/non-dispatchable plant in Northern Ireland (MW) | Appendix 3
| Table A3.5 | All renewable energy sources in Northern Ireland (MW) | Appendix 3

## Demand - IE
Demand Forecast for Ireland
4.2.2 Economic forecast
Table 4.1 Average annual growth rates for macroeconomic parameters, values used for median demand as advised by the ESRI
|  | 2024-2025 |  |  | 2026-2030 |  |  | 2031-2035
|  | Low (75% ESRI) | Median (ESRI) | High (110% ESRI) | Low (75% ESRI) | Median (ESRI) | High (110% ESRI) | Low (75% ESRI) | Median (ESRI) | High (110% ESRI)
| Real GNI* | 2.4% | 3.2% | 3.5% | 2.3% | 3% | 3.3% | 1.9% | 2.5% | 2.8%
| Personal Consumption | 2% | 2.6% | 2.9% | 1.9% | 2.5% | 2.8% | 1.5% | 2% | 2.2%
4.2.3 Data centres and new technology loads
Table 4.2 Forecasted data centre and new technology load demand by 2035. 2024 demand 959 MVA
| Forecast Scenario | Growth from 2024-2035 (MVA) | 2035 Demand (MVA)
| Low | 443 | 1402
| Median | 911 | 1870
| High | 1225 | 2183
Figure 4.1 Ireland demand expected from assumed build out of data centres and new technology loads
| Year | Historic (MVA) | AIRAA25
Peak Transmission (MW)
|  |  | Low (MVA) | Median (MVA) | High (MVA) | Contract Ramp (MVA)
| 2016 | 196.5
| 2017 | 262
| 2018 | 357.24
| 2019 | 431.5
| 2020 | 519.7759
| 2021 | 600.1
| 2022 | 733.5
| 2023 | 867
| 2024 |  | 959 | 959 | 959 | 1494
| 2025 |  | 997 | 1082 | 1156 | 1720
| 2026 |  | 1042 | 1209 | 1368 | 2114
| 2027 |  | 1087 | 1307 | 1522 | 2156
| 2028 |  | 1132 | 1396 | 1658 | 2221
| 2029 |  | 1179 | 1486 | 1793 | 2328
| 2030 |  | 1226 | 1577 | 1912 | 2366
| 2031 |  | 1264 | 1659 | 2000 | 2373
| 2032 |  | 1301 | 1727 | 2077 | 2373
| 2033 |  | 1336 | 1788 | 2121 | 2373
| 2034 |  | 1369 | 1831 | 2157 | 2373
| 2035 |  | 1402 | 1870 | 2183 | 2373
4.2.4 Electrification of heat and transport
Table 4.3 2030 EV & HP projections from SEAI's WEM Scenario in Median Scenario versus Climate Action Plan Targets 2024
| Year: 2030 |  | WEM (Median Scenario) | Climate Action Plan 2024
| Electric Vehicles |  | 768000 | 927000
| Heat Pumps | Retrofit | 240000 | 400000
|  | New Build | 426000 | 280000
|  | Commercial | 9100 | 50000
Table 4.4 Low, median and high Total Electricity Requirement key assumption differences by 2030
|  | Retrofit Heat Pumps | New Build Heat Pumps | Electric Vehicles
| Low | 75% SEAI WEM | Current Housing Trajectory c.35k/year | 75% SEAI WEM
| Median | SEAI WEM (240k) | Gov Housing Targets (c. 50k/year) + Existing (126k) | SEAI WEM (768k)
| High | SEAI WAM (362k) | Gov Housing Targets (c. 50k/year) + Lower COP | SEAI WAM (920k)
Figure 4.2 Electric vehicle electrical energy demand - median scenario
| Year | BEVs (TWh) | PHEVs (TWh) | Commercial (TWh) | Total (TWh)
| 2022 | 0.08 | 0.05 | 0.02 | 0.15
| 2023 | 0.13 | 0.07 | 0.02 | 0.22
| 2024 | 0.17 | 0.1 | 0.04 | 0.31
| 2025 | 0.28 | 0.16 | 0.08 | 0.52
| 2026 | 0.39 | 0.21 | 0.17 | 0.77
| 2027 | 0.49 | 0.26 | 0.23 | 0.98
| 2028 | 0.58 | 0.31 | 0.29 | 1.18
| 2029 | 0.66 | 0.36 | 0.34 | 1.36
| 2030 | 0.73 | 0.41 | 0.39 | 1.53
| 2031 | 0.82 | 0.46 | 0.44 | 1.72
| 2032 | 0.9 | 0.52 | 0.5 | 1.92
| 2033 | 0.97 | 0.58 | 0.55 | 2.1
| 2034 | 1.05 | 0.64 | 0.6 | 2.29
| 2035 | 1.12 | 0.7 | 0.65 | 2.47
Figure 4.2 Heat pump electrical energy demand - median scenario
| Year | New Builds - Residential (TWh) | Retrofits - Residential (TWh) | Commercial (TWh) | Total (TWh)
| 2022 | 0.04 | 0.18 | 0.14 | 0.36
| 2023 | 0.14 | 0.25 | 0.14 | 0.53
| 2024 | 0.28 | 0.25 | 0.15 | 0.68
| 2025 | 0.28 | 0.35 | 0.22 | 0.85
| 2026 | 0.35 | 0.52 | 0.23 | 1.1
| 2027 | 0.42 | 0.68 | 0.24 | 1.34
| 2028 | 0.5 | 0.83 | 0.25 | 1.58
| 2029 | 0.58 | 0.98 | 0.26 | 1.82
| 2030 | 0.67 | 1.12 | 0.27 | 2.06
| 2031 | 0.73 | 1.26 | 0.28 | 2.27
| 2032 | 0.79 | 1.39 | 0.29 | 2.47
| 2033 | 0.85 | 1.52 | 0.29 | 2.66
| 2034 | 0.91 | 1.64 | 0.3 | 2.85
| 2035 | 0.96 | 1.76 | 0.31 | 3.03
4.2.5 Temperature correction
Figure 4.3 Historic recorded and temperature corrected peak demand
| Year | Network Exported Peak (MW) | Historic Temperature-Corrected Peak (MW)
| 2007/08 | 4914 | 5110
| 2008/09 | 4891 | 4900
| 2009/10 | 4992 | 4870
| 2010/11 | 5090 | 4900
| 2011/12 | 4640 | 4820
| 2012/13 | 4589 | 4730
| 2013/14 | 4523 | 4800
| 2014/15 | 4695 | 4890
| 2015/16 | 4668 | 4970
| 2016/17 | 4751.87 | 4970
| 2017/18 | 4939.61 | 5050
| 2018/19 | 4910 | 5180
| 2019/20 | 5007 | 5150
| 2020/21 | 5335 | 5370
| 2021/22 | 5346 | 5530
| 2022/23 | 5508.36 | 5470
| 2023/24 | 5567 | 5653.3638
| 2024/25 | 6024 | 5912
4.2.6 Demand flexibility
Figure 4.4 Impact of demand flexibility on 2030 peak day (median scenario)
| Hr | No Flexibility Services or Incentives (MW) | 12% Residential Demand Reduction and Flexible EV Charging Profile (MW) | 12% Residential Demand Reduction from Flexibility Services & Incentives (MW)
| 0 | 5231.336 | 5420.511 | 5157.073
| 1 | 4852.404 | 5152.362 | 4826.226
| 2 | 4694.849 | 5030.573 | 4670.907
| 3 | 4579.121 | 4840.201 | 4556.822
| 4 | 4502.028 | 4693.1 | 4480.824
| 5 | 4609.222 | 4674.081 | 4586.496
| 6 | 5094.016 | 5061.391 | 5064.407
| 7 | 5932.045 | 5780.663 | 5847.835
| 8 | 6273.94 | 6026.475 | 6184.876
| 9 | 6361.546 | 6129.643 | 6271.239
| 10 | 6323.604 | 6136.734 | 6233.835
| 11 | 6312.548 | 6153.756 | 6222.936
| 12 | 6372.176 | 6209.691 | 6281.718
| 13 | 6342.945 | 6172.064 | 6252.902
| 14 | 6322.019 | 6158.984 | 6232.273
| 15 | 6419.045 | 6192.777 | 6327.922
| 16 | 6807.837 | 6523.188 | 6711.195
| 17 | 7149.719 | 6791.551 | 7048.223
| 18 | 7185.136 | 6761.067 | 7083.137
| 19 | 7041.764 | 6695.626 | 6941.801
| 20 | 6769.592 | 6497.687 | 6673.492
| 21 | 6392.061 | 6200.24 | 6301.32
| 22 | 5895.772 | 5781.991 | 5812.077
| 23 | 5423.598 | 5677.271 | 5389.311
Figure 4.5 Impact of demand flexibility in median scenario across the study period
| Year | No Flexibility Services or Incentives (MW) | 12% Residential Demand Reduction from Flexibility Services & Incentives (MW) | 12% Residential Demand Reduction and Flexible EV Charging Profile (MW)
| 2023 | 5775.0555 | 5775.0555 | 5761.9627
| 2024 | 6046.6868 | 6046.6868 | 6019.3511
| 2025 | 6263.2878 | 6216.7878 | 6155.6556
| 2026 | 6443.9767 | 6386.5873 | 6285.1073
| 2027 | 6629.6986 | 6561.0983 | 6418.6138
| 2028 | 6813.521 | 6733.6407 | 6546.7296
| 2029 | 6997.9959 | 6906.8135 | 6672.6494
| 2030 | 7178.6648 | 7076.2268 | 6792.584
| 2031 | 7332.6858 | 7219.453 | 6899.5331
| 2032 | 7470.689 | 7346.7822 | 6991.3504
| 2033 | 7599.1664 | 7464.7037 | 7074.5427
| 2034 | 7706.8601 | 7561.9626 | 7137.8697
| 2035 | 7807 | 7652.1468 | 7194.9104
4.2.8 Total Electricity Requirement (TER)
Figure 4.6 Total Electricity Requirement for Ireland
| Year | Historical (TWh) | All Island Resource Adequacy Assessment (TWh)
|  |  | AIRAA25 Low* | AIRAA25 Median* | AIRAA25 High* | AIRAA24 Low | AIRAA24 Median | AIRAA24 High
| 2017 | 29.37
| 2018 | 29.8
| 2019 | 30.6
| 2020 | 30.86
| 2021 | 32.16
| 2022 | 33.03
| 2023 | 33.93
| 2024 | 35.2 | 35.2005 | 35.2005 | 35.2005 | 35.061 | 35.846 | 36.3535
| 2025 |  | 36.5217 | 37.1949 | 37.703 | 35.7293 | 37.7266 | 39.1782
| 2026 |  | 37.3074 | 38.9624 | 40.4003 | 36.5907 | 39.4992 | 41.8684
| 2027 |  | 38.079 | 40.5856 | 42.8577 | 37.3883 | 41.1078 | 44.0519
| 2028 |  | 38.7257 | 41.9377 | 44.8553 | 37.9983 | 42.3642 | 45.6859
| 2029 |  | 39.364 | 43.2544 | 46.7622 | 38.5965 | 43.5465 | 47.2058
| 2030 |  | 39.9955 | 44.5555 | 48.5568 | 39.1709 | 44.6697 | 48.5474
| 2031 |  | 40.5512 | 45.7272 | 50.03 | 39.8869 | 45.9511 | 49.8327
| 2032 |  | 41.05 | 46.7766 | 51.2885 | 40.606 | 47.1819 | 50.9169
| 2033 |  | 41.5264 | 47.7203 | 52.3277 | 41.3154 | 48.3764 | 51.949
| 2034 |  | 41.9763 | 48.5353 | 53.1545 | 42.0151 | 49.5152 | 52.9815
| 2035 |  | 42.4128 | 49.2329 | 53.8826
* AIRAA25 Low, Median, High data for year 2024 is based on historic data for charting purposes, forecast begins in year 2025.
Table 4.5 Low, median and high Total Electricity Requirement key assumption differences by 2030
|  |  | Low | Median | High
| Housing |  | Based on macro-economic projections from ESRI | Gov housing targets achieved (c. 50k houses per annum) | Gov housing targets + reduced efficiency gain
| Heat Pumps | Retrofit | 75% SEAI WEM | SEAI WEM (240k) | SEAI WAM (362k)
|  | New Builds | Current housing trajectory (c. 35k/year) | Gov housing targets (c. 50k/year) + existing (126k) | Gov housing targets (c. 50k/year) + lower COP
| Electric Vehicles |  | 75% SEAI WEM | SEAI WEM (768k) | SEAI WAM (920k)
| Data Centre and New Technology Loads |  | Low Ramp | Median Ramp | High Ramp
| Economic Growth |  | 75% ESRI Economic Projection | 100% ESRI Economic Projection | 110% ESRI Economic Projection
| Industrial Heat |  | 75% SEAI's National Energy Projections 2024 WEM Scenario | SEAI's National Energy Projections 2024 WEM Scenario | 110% SEAI's National Energy Projections 2024 WEM Scenario
Figure 4.7 Ireland median demand Total Electricity Requirement sectoral breakdown
|  | Residential (TWh) | Commercial (TWh) | Industrial (TWh) | Electric Vehicles (TWh) | Heat Pumps (TWh) | Data Centres & New Tech Loads (TWh) | TER incorporating losses (TWh)
| 2020 | 8.9731 | 8.5497 | 6.4498 | 0.045289 | 0.35496 | 4.1552 | 30.9
| 2021 | 9.003 | 8.9028 | 6.7161 | 0.089911 | 0.42411 | 4.8916 | 32.2
| 2022 | 8.4977 | 9.192 | 6.9343 | 0.15534 | 0.35333 | 5.8252 | 33
| 2023 | 8.2448 | 9.0274 | 6.8101 | 0.22975 | 0.52979 | 6.9984 | 33.9
| 2024 | 8.5486 | 9.037 | 6.8174 | 0.30777 | 0.67725 | 7.9812 | 35.2
| 2025 | 8.6708 | 8.0932 | 7.8017 | 0.5187 | 0.85389 | 8.9116 | 37.2
| 2026 | 8.7677 | 8.0778 | 7.7991 | 0.77234 | 1.0968 | 10.0053 | 39
| 2027 | 8.8836 | 8.0624 | 7.7976 | 0.98308 | 1.338 | 10.9908 | 40.6
| 2028 | 8.9893 | 8.0149 | 7.7659 | 1.1793 | 1.581 | 11.8098 | 41.9
| 2029 | 9.1156 | 7.9677 | 7.7348 | 1.3611 | 1.8241 | 12.5886 | 43.3
| 2030 | 9.2401 | 7.9207 | 7.7044 | 1.5282 | 2.0578 | 13.3785 | 44.6
| 2031 | 9.2926 | 7.8639 | 7.6655 | 1.7236 | 2.2662 | 14.1346 | 45.7
| 2032 | 9.3438 | 7.8074 | 7.6271 | 1.915 | 2.4668 | 14.7883 | 46.8
| 2033 | 9.3937 | 7.7514 | 7.5897 | 2.1021 | 2.6599 | 15.354 | 47.7
| 2034 | 9.4423 | 7.6958 | 7.5532 | 2.2849 | 2.8461 | 15.8104 | 48.5
| 2035 | 9.4898 | 7.6406 | 7.5176 | 2.4635 | 3.0256 | 16.1658 | 49.2
Figure 4.8 Sectoral contribution to Ireland's Median TER in 2026 & 2035
|  | 2026 (TWh) | 2035 (TWh)
| Residential | 8.7677 | 9.4898
| Commercial | 8.0778 | 7.6406
| Industrial | 7.7991 | 7.5176
| Electric Vehicles | 0.77234 | 2.4635
| Heat Pumps | 1.0968 | 3.0256
| Data Centres & New Tech Loads | 10.0053 | 16.1658
4.2.9 Peak Demand
Figure 4.9 Sectoral contribution to Ireland's peak demand in 2026 & 2035
|  | 2026 (MW) | 2035 (MW)
| Residential, Commercial & Industrial | 4724 | 4448
| Electric Vehicles | 91 | 157
| Heat Pumps | 261 | 720
| Data Centres & New Tech Loads | 1209 | 1870
Figure 4.10 Transmission peak forecast for Ireland
| Year | Historical (MW) | All Island Resource Adequacy Assessment
|  |  | AIRAA25 Low* | AIRAA25 Median* | AIRAA25 High* | AIRAA24 Low* | AIRAA24 Median* | AIRAA24 High*
| 2016 | 4902.9202
| 2017 | 5017.2312
| 2018 | 5126.2703
| 2019 | 5112.3603
| 2020 | 5341.0803
| 2021 | 5507.2416
| 2022 | 5474.4813
| 2023 | 5653.3638
| 2024 | 5911.6954 | 5652 | 5834 | 5970 | 5911.6954 | 5911.6954 | 5911.6954
| 2025 |  | 5869.4414 | 6044.1458 | 6153.7406 | 5735.5032 | 6019.7669 | 6276.2304
| 2026 |  | 5886.7702 | 6173.295 | 6402.9312 | 5815.1331 | 6210.6137 | 6557.5861
| 2027 |  | 5934.2967 | 6306.5029 | 6624.648 | 5882.7836 | 6347.0493 | 6754.442
| 2028 |  | 5981.0803 | 6434.5943 | 6828.7132 | 5929.0902 | 6456.0135 | 6917.489
| 2029 |  | 6025.083 | 6561.623 | 7029.1188 | 5948.8634 | 6527.2062 | 7032.0121
| 2030 |  | 6063.2297 | 6681.9084 | 7201.8155 | 5975.3191 | 6608.1245 | 7141.2095
| 2031 |  | 6097.0642 | 6788.4558 | 7341.5653 | 6030.7258 | 6713.208 | 7245.366
| 2032 |  | 6129.4738 | 6880.3677 | 7468.0534 | 6078.5982 | 6806.8691 | 7336.7244
| 2033 |  | 6158.9752 | 6963.8011 | 7559.8091 | 6139.4462 | 6914.9829 | 7442.4588
| 2034 |  | 6185.389 | 7026.9137 | 7639.0952 | 6200.5158 | 7010.9674 | 7549.0341
| 2035 |  | 6211.2685 | 7083.616 | 7707.5947
* Data for year 2024 is based on historic data for charting purposes, forecast begins in year 2025.
4.2.10 Demand shape
Figure 4.11 Forecast hourly demand shape in Ireland
2025 All Island Resource Adequacy Assessment (MW)
| Hour | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| 0 | 3815 | 4031 | 4232 | 4403 | 4584 | 4756 | 4890 | 5018 | 5159 | 5272 | 5365
| 1 | 3652 | 3867 | 4067 | 4236 | 4422 | 4601 | 4728 | 4851 | 4987 | 5095 | 5185
| 2 | 3577 | 3787 | 3983 | 4150 | 4333 | 4511 | 4630 | 4746 | 4876 | 4980 | 5068
| 3 | 3495 | 3690 | 3868 | 4018 | 4183 | 4340 | 4432 | 4531 | 4641 | 4730 | 4803
| 4 | 3439 | 3623 | 3783 | 3917 | 4062 | 4201 | 4276 | 4362 | 4460 | 4536 | 4598
| 5 | 3520 | 3687 | 3836 | 3951 | 4077 | 4195 | 4256 | 4326 | 4409 | 4470 | 4518
| 6 | 3798 | 3963 | 4110 | 4219 | 4351 | 4471 | 4553 | 4624 | 4708 | 4767 | 4816
| 7 | 4190 | 4366 | 4518 | 4628 | 4769 | 4895 | 5004 | 5089 | 5190 | 5259 | 5326
| 8 | 4419 | 4608 | 4778 | 4896 | 5042 | 5167 | 5285 | 5375 | 5485 | 5561 | 5636
| 9 | 4541 | 4744 | 4931 | 5068 | 5230 | 5372 | 5504 | 5604 | 5726 | 5816 | 5898
| 10 | 4541 | 4744 | 4934 | 5073 | 5239 | 5388 | 5534 | 5638 | 5763 | 5856 | 5936
| 11 | 4529 | 4731 | 4922 | 5062 | 5230 | 5381 | 5534 | 5641 | 5767 | 5861 | 5940
| 12 | 4546 | 4748 | 4940 | 5080 | 5247 | 5399 | 5556 | 5663 | 5790 | 5886 | 5964
| 13 | 4487 | 4689 | 4880 | 5019 | 5186 | 5336 | 5495 | 5604 | 5732 | 5828 | 5906
| 14 | 4440 | 4641 | 4831 | 4968 | 5135 | 5284 | 5442 | 5551 | 5678 | 5773 | 5851
| 15 | 4461 | 4655 | 4835 | 4964 | 5120 | 5260 | 5409 | 5511 | 5631 | 5719 | 5793
| 16 | 4630 | 4828 | 5011 | 5142 | 5299 | 5438 | 5589 | 5690 | 5810 | 5901 | 5980
| 17 | 4847 | 5051 | 5238 | 5374 | 5530 | 5667 | 5815 | 5916 | 6039 | 6134 | 6217
| 18 | 4892 | 5102 | 5294 | 5432 | 5588 | 5723 | 5872 | 5976 | 6101 | 6198 | 6283
| 19 | 4846 | 5069 | 5273 | 5425 | 5596 | 5746 | 5903 | 6016 | 6151 | 6259 | 6352
| 20 | 4682 | 4910 | 5114 | 5268 | 5442 | 5596 | 5750 | 5868 | 6005 | 6114 | 6208
| 21 | 4450 | 4678 | 4885 | 5039 | 5217 | 5377 | 5536 | 5656 | 5794 | 5901 | 5993
| 22 | 4150 | 4363 | 4555 | 4704 | 4875 | 5035 | 5189 | 5311 | 5447 | 5549 | 5635
| 23 | 3955 | 4172 | 4375 | 4547 | 4745 | 4931 | 5097 | 5237 | 5390 | 5509 | 5609
Figure 4.12 Electric vehicle charging profiles
| Hour | Simple | Passenger Smarter | BEV LCV | BEV Buses
| 0 | 3.323% | 10.5% | 11% | 8.9%
| 1 | 2.169% | 10.5% | 11% | 8.7%
| 2 | 1.327% | 10.5% | 11% | 8.5%
| 3 | 0.8442% | 7.6% | 10% | 8.1%
| 4 | 0.6273% | 5% | 10% | 6.5%
| 5 | 0.5839% | 3% | 2% | 6%
| 6 | 0.8572% | 1% | 0.4538% | 1.5%
| 7 | 2.01% | 1% | 0.4538% | 2%
| 8 | 4.292% | 1% | 0.4538% | 2%
| 9 | 5.383% | 3% | 0.4538% | 2%
| 10 | 4.249% | 3% | 0.4538% | 1.75%
| 11 | 3.541% | 3% | 0.4538% | 1.75%
| 12 | 3.455% | 2.8% | 0.4538% | 1.75%
| 13 | 3.679% | 2.8% | 0.4538% | 1.65%
| 14 | 3.489% | 2.8% | 0.4538% | 1.65%
| 15 | 3.677% | 1% | 0.4538% | 1.65%
| 16 | 4.99% | 1% | 0.4538% | 2%
| 17 | 6.708% | 1% | 0.4538% | 2.3%
| 18 | 8.671% | 1.4% | 0.4538% | 2.3%
| 19 | 9.098% | 4% | 2% | 3.5%
| 20 | 8.426% | 4.3% | 6.1% | 3.8%
| 21 | 7.341% | 4.5% | 9% | 4.5%
| 22 | 6.276% | 4.7% | 11% | 8.6%
| 23 | 4.984% | 10.6% | 11% | 8.6%
Data Centre Demand
|  | Historical (MW) | 2025 All Island Resource Adequacy Assessment
| Year |  | Low | Median | High
| 2016 | 134.1
| 2017 | 174.4
| 2018 | 256.24
| 2019 | 319
| 2020 | 409.7759
| 2021 | 490.1
| 2022 | 600.5
| 2023 | 717
| 2024 | 794.5 | 794.5 | 794.5 | 794.5
| 2025 |  | 822.5 | 902.7 | 971.9
| 2026 |  | 857.5 | 1014.9 | 1163.8
| 2027 |  | 892.5 | 1098.3 | 1298.4
| 2028 |  | 927.5 | 1172.4 | 1413.8
| 2029 |  | 964.5 | 1246.6 | 1529.1
| 2030 |  | 1002 | 1323.25 | 1628.09
| 2031 |  | 1039 | 1389.7 | 1695.99
| 2032 |  | 1076 | 1451.9 | 1752.89
| 2033 |  | 1110.75 | 1513.2 | 1796.47
| 2034 |  | 1143.75 | 1556.4 | 1831.595
| 2035 |  | 1176.75 | 1594.57 | 1858.07

## Demand - NI
Demand Forecast for Northern Ireland
4.3.3 Data Centres
Figure 4.13 Northern Ireland TER expected from data centres across demand scenarios
| Year | Low (TWh) | Median (TWh) | High (TWh)
| 2025 | 0 | 0 | 0
| 2026 | 0 | 0 | 0
| 2027 | 0 | 0 | 0
| 2028 | 0 | 0 | 0
| 2029 | 0 | 0.0219 | 0.04
| 2030 | 0 | 0.0438 | 0.07
| 2031 | 0 | 0.0657 | 0.11
| 2032 | 0 | 0.0876 | 0.15
| 2033 | 0 | 0.0876 | 0.15
| 2034 | 0 | 0.0876 | 0.15
| 2035 | 0 | 0.0876 | 0.15
4.3.4 Electrification of heat and transport
Table 4.6 Number of electric vehicle and heat pump installations included in the low, median, and high demand forecast
|  | Low |  | Median |  | High
|  | Electric Vehicles | Heat Pump Installations | Electric Vehicles | Heat Pump Installations | Electric Vehicles | Heat Pump Installations
| 2025 | 56000 | 2000 | 70000 | 2500 | 83000 | 3000
| 2030 | 194000 | 34400 | 242000 | 43000 | 291000 | 51500
| 2035 | 390000 | 115000 | 487000 | 143700 | 585000 | 172500
4.3.5 Total Electricity Requirement forecast
Table 4.7 Low, median and high Total Electricity Requirement key assumption differences for Northern Ireland
|  |  | Low | Median | High
| Number of Electric Vehicles |  | DfI Transport Emissions Model Projections Less 20% | DfI Transport Emissions Model Projections | DfI Transport Emissions Model Projections Plus 20%
| Number of Heat Pumps |  | NIE Networks Constrained Growth Scenario Projections Less 20% | NIE Networks Constrained Growth Scenario Projections | NIE Networks Constrained Growth Scenario Projections Plus 20%
| Data Centre and New Technology Loads |  | None | Median Ramp | High Ramp
| Economic Growth Projection |  | Oxford Economics Ten Year Forecast Less 1% | Oxford Economics Ten Year Forecast | Oxford Economics Ten Year Forecast Plus 1%
Figure 4.14 Northern Ireland total electricity requirement (TER) forecast
| Year | Historical (TWh) | AIRAA 2024** |  |  | AIRAA 2025*
|  |  | Low (TWh) | Median (TWh) | High (TWh) | Low (TWh) | Median (TWh) | High (TWh)
| 2010 | 9.2103
| 2011 | 9.1752
| 2012 | 9.0701
| 2013 | 9.0324
| 2014 | 9.0493
| 2015 | 9.0489
| 2016 | 9.0176
| 2017 | 8.7723
| 2018 | 8.9708
| 2019 | 8.7054
| 2020 | 8.3295
| 2021 | 8.5565
| 2022 | 8.3537
| 2023 | 8.1115 | 8.11 | 8.11 | 8.11
| 2024 | 8.1593 | 7.95 | 8.21 | 8.53 | 8.1593 | 8.1593 | 8.1593
| 2025 |  | 8.02 | 8.33 | 8.68 | 7.9486 | 8.1875 | 8.5493
| 2026 |  | 8.14 | 8.57 | 8.94 | 8.0173 | 8.2989 | 8.7044
| 2027 |  | 8.34 | 9.05 | 9.49 | 8.1674 | 8.4952 | 8.9493
| 2028 |  | 8.53 | 9.31 | 9.81 | 8.3222 | 8.6979 | 9.2023
| 2029 |  | 8.72 | 9.58 | 10.15 | 8.4813 | 8.9282 | 9.5027
| 2030 |  | 8.92 | 9.83 | 10.49 | 8.6435 | 9.1629 | 9.7988
| 2031 |  | 9.13 | 10.11 | 10.84 | 8.8682 | 9.4762 | 10.1996
| 2032 |  | 9.34 | 10.47 | 11.29 | 9.0937 | 9.7907 | 10.6024
| 2033 |  | 9.56 | 10.71 | 11.61 | 9.3205 | 10.0853 | 10.9678
| 2034 |  | 9.77 | 10.94 | 11.92 | 9.5473 | 10.3801 | 11.3338
| 2035 |  |  |  |  | 9.7727 | 10.6735 | 11.6985
* AIRAA25 Low, Median, High data for year 2024 is based on historic data for charting purposes, forecast begins in year 2025.
** AIRAA24 Low, Median, High data for year 2023 is based on historic data for charting purposes, forecast begins in year 2024.
Figure 4.15 Northern Ireland median total electricity requirement (TER) forecast components
|  | Conventional Demand | Electric Vehicles | Heat Pumps | Data Centres & New Tech Loads
| 2020 | 8.3185 | 0.01103 | 0 | 0
| 2021 | 8.5344 | 0.020541 | 0.0015393 | 0
| 2022 | 8.3125 | 0.03831 | 0.002984 | 0
| 2023 | 8.0437 | 0.062011 | 0.0057878 | 0
| 2024 | 8.0185 | 0.13105 | 0.0098276 | 0
| 2025 | 7.9804 | 0.19003 | 0.017097 | 0
| 2026 | 7.97 | 0.25881 | 0.070147 | 0
| 2027 | 8.0371 | 0.33793 | 0.12018 | 0
| 2028 | 8.1034 | 0.42712 | 0.16738 | 0
| 2029 | 8.1691 | 0.52527 | 0.21194 | 0.0219
| 2030 | 8.2345 | 0.63057 | 0.25401 | 0.0438
| 2031 | 8.2994 | 0.74083 | 0.37019 | 0.0657
| 2032 | 8.3638 | 0.85484 | 0.4845 | 0.0876
| 2033 | 8.4288 | 0.97192 | 0.59696 | 0.0876
| 2034 | 8.494 | 1.091 | 0.70759 | 0.0876
| 2035 | 8.5589 | 1.2106 | 0.81641 | 0.0876
Figure 4.16 Northern Ireland's total electricity requirement (TER) breakdown in 2026 and 2035
|  | 2026 (TWh) | 2035 (TWh)
| Conventional Demand | 7.97 | 8.5589
| Electric Vehicles | 0.25881 | 1.2106
| Heat Pumps | 0.070147 | 0.81641
| Data Centres & New Tech Loads | 0 | 0.0876
4.3.6 Peak demand forecasting
Figure 4.17 Northern Ireland's total electricity requirement (TER) peak demand breakdown in 2026 and 2035
|  | 2026 TER Peak (MW) | 2035 TER Peak (MW)
| Conventional Demand | 1612.21 | 1725.74
| Electric Vehicles | 19.41 | 47.98
| Heat Pumps | 19.16 | 279.07
| Data Centres & New Tech Loads | 0 | 14.64
Figure 4.18 ACS Transmission Peak forecasts for Northern Ireland
| Year | Historical (MW) | AIRAA 2024** |  |  | AIRAA 2025*
|  |  | Low (MW) | Median (MW) | High (MW) | Low (MW) | Median (MW) | High (MW)
| 2020 | 1616.2048
| 2021 | 1602.7787
| 2022 | 1629.5739
| 2023 | 1563.8798 | 1563.8798 | 1563.8798 | 1563.8798
| 2024 | 1616.4479 | 1450 | 1560 | 1670 | 1616.4479 | 1616.4479 | 1616.4479
| 2025 |  | 1460 | 1570 | 1690 | 1542.3902 | 1588.3143 | 1660.8421
| 2026 |  | 1490 | 1630 | 1750 | 1557.5265 | 1610.7757 | 1690.8648
| 2027 |  | 1530 | 1710 | 1830 | 1588.0452 | 1648.824 | 1737.001
| 2028 |  | 1570 | 1760 | 1890 | 1613.9958 | 1686.2072 | 1777.6471
| 2029 |  | 1600 | 1800 | 1940 | 1638.1974 | 1717.3716 | 1816.1714
| 2030 |  | 1630 | 1840 | 1980 | 1665.0363 | 1752.1807 | 1858.5517
| 2031 |  | 1660 | 1880 | 2040 | 1713.4386 | 1810.9268 | 1928.1227
| 2032 |  | 1690 | 1910.0857 | 2110 | 1755.1329 | 1857.3203 | 1988.3325
| 2033 |  | 1720 | 1960 | 2160 | 1809.2432 | 1921.6025 | 2063.4947
| 2034 |  | 1750 | 2000 | 2210 | 1851.3459 | 1973.344 | 2125.7942
| 2035 |  |  |  |  | 1895.6276 | 2027.4315 | 2190.1302
* AIRAA25 Low, Median, High data for year 2024 is based on historic data for charting purposes, forecast begins in year 2025.
** AIRAA24 Low, Median, High data for year 2023 is based on historic data for charting purposes, forecast begins in year 2024.
4.3.7 Demand Flexibility: Impact of Off-Peak Charging
Figure 4.19 The impact of demand flexibility on 2030 peak day for Northern Ireland (median scenario)
|  | Sensitivity - No Flexibility in EV Charging | Median Scenario | Sensitivity - All EV Charging Off Peak
| 0 | 901.3225 | 971.9854 | 1002.2706
| 1 | 879.8265 | 960.7253 | 995.3972
| 2 | 841.8183 | 930.887 | 969.0603
| 3 | 814.052 | 907.8117 | 947.9954
| 4 | 815.8354 | 883.5417 | 912.5597
| 5 | 865.3907 | 908.272 | 926.6508
| 6 | 1018.5725 | 1039.3784 | 1048.2965
| 7 | 1256.927 | 1247.1219 | 1242.9214
| 8 | 1410.5087 | 1378.5369 | 1364.8364
| 9 | 1480.2546 | 1437.6894 | 1419.4491
| 10 | 1497.9248 | 1485.7907 | 1480.5922
| 11 | 1506.5869 | 1501.3299 | 1499.0788
| 12 | 1539.6501 | 1535.2332 | 1533.3422
| 13 | 1535.7124 | 1527.1795 | 1523.5245
| 14 | 1525.7004 | 1519.0096 | 1516.144
| 15 | 1562.5029 | 1553.9903 | 1550.344
| 16 | 1703.8449 | 1665.1035 | 1648.5022
| 17 | 1841.6119 | 1786.1871 | 1762.4359
| 18 | 1751.4956 | 1677.0041 | 1645.0813
| 19 | 1638.6649 | 1563.9127 | 1531.8781
| 20 | 1516.5092 | 1473.5261 | 1455.1066
| 21 | 1374.8109 | 1345.2772 | 1332.6215
| 22 | 1217.4901 | 1200.2475 | 1192.8593
| 23 | 1054.8888 | 1052.1328 | 1050.9529
Figure 4.20 Impact of demand flexibility in median scenario across the study period for Northern Ireland
|  | Sensitivity - No Flexibility in EV Charging | Median Scenario | Sensitivity - All EV Charging Off Peak
| 2025 | 1629.2369 | 1628.3143 | 1620.0125
| 2026 | 1654.7563 | 1650.7757 | 1634.8517
| 2027 | 1698.5189 | 1688.824 | 1666.2056
| 2028 | 1744.7542 | 1726.2072 | 1698.3858
| 2029 | 1794.2491 | 1757.3716 | 1732.9904
| 2030 | 1847.6055 | 1792.1807 | 1768.4295
| 2031 | 1928.2443 | 1850.9268 | 1831.6601
| 2032 | 2001.8835 | 1897.3203 | 1885.8472
| 2033 | 2085.124 | 1961.6025 | 1948.0144
| 2034 | 2154.2328 | 2013.344 | 1998.2481
| 2035 | 2229.5664 | 2067.4315 | 2049.79
4.3.8 Shape of the Demand Profile
Figure 4.21 Historical and forecast hourly demand shape in Northern Ireland
2026-35 All Island Resource Adequacy Assessment (MW)
| Hour | Historical | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| 0 | 674.1 | 674.6672 | 687.7337 | 713.7254 | 743.7986 | 789.8153 | 836.3415 | 895.724 | 955.7644 | 1008.3939 | 1058.9714 | 1109.4902
| 1 | 663.2 | 669.6856 | 681.5282 | 706.0278 | 734.9517 | 781.4435 | 827.9209 | 887.6293 | 948.7648 | 1000.7531 | 1050.92 | 1100.9412
| 2 | 652.3 | 650.8918 | 662.3132 | 685.89 | 713.8865 | 760.7951 | 806.9243 | 867.0096 | 929.3658 | 981.1188 | 1030.9926 | 1080.8321
| 3 | 640.3 | 636.8506 | 648.1669 | 671.197 | 698.629 | 745.782 | 791.5705 | 851.8594 | 914.9179 | 966.5156 | 1016.2187 | 1065.9476
| 4 | 646.2 | 645.2957 | 655.1391 | 675.3183 | 698.407 | 737.041 | 774.3792 | 824.2859 | 875.2871 | 918.8506 | 960.3016 | 1001.7102
| 5 | 676.7 | 708.0253 | 717.0099 | 734.9197 | 754.6769 | 786.3523 | 816.0586 | 857.1794 | 896.9476 | 933.8293 | 968.3891 | 1002.7825
| 6 | 785.7 | 840.4103 | 851.3121 | 868.3629 | 886.2173 | 913.4696 | 935.0101 | 969.968 | 1000.5321 | 1033.0398 | 1062.8895 | 1092.6343
| 7 | 931.9 | 975.4754 | 990.0114 | 1007.7981 | 1024.4273 | 1046.6476 | 1061.0713 | 1086.3942 | 1106.9737 | 1135.5398 | 1160.7616 | 1186.1893
| 8 | 1005.9 | 1050.881 | 1068.0216 | 1089.0643 | 1107.9824 | 1129.6124 | 1144.6821 | 1167.3511 | 1184.819 | 1214.5965 | 1240.6036 | 1266.996
| 9 | 1047.3 | 1084.9017 | 1100.2454 | 1122.5651 | 1142.6788 | 1163.7156 | 1180.7426 | 1203.8145 | 1219.3562 | 1249.6644 | 1275.925 | 1302.347
| 10 | 1057 | 1088.8479 | 1101.4868 | 1123.9931 | 1145.9709 | 1173.0518 | 1197.0058 | 1228.3281 | 1252.9726 | 1287.6093 | 1318.4546 | 1349.3136
| 11 | 1057.3 | 1088.103 | 1098.5119 | 1119.984 | 1141.324 | 1168.3875 | 1192.9285 | 1225.0013 | 1250.0536 | 1283.9459 | 1314.1824 | 1344.2039
| 12 | 1060.1 | 1075.5414 | 1084.844 | 1105.8809 | 1127.0178 | 1153.6878 | 1178.3764 | 1210.8502 | 1235.6125 | 1268.8402 | 1298.6522 | 1328.068
| 13 | 1027.1 | 1049.0363 | 1058.0464 | 1078.6865 | 1099.4929 | 1125.0026 | 1148.8929 | 1180.6677 | 1204.0074 | 1236.0764 | 1264.9519 | 1293.3958
| 14 | 1017.7 | 1037.5371 | 1046.7905 | 1066.9745 | 1087.4663 | 1112.9695 | 1136.2646 | 1167.7046 | 1191.1119 | 1222.7829 | 1251.3476 | 1279.5645
| 15 | 1040.9 | 1073.802 | 1084.3174 | 1105.1279 | 1125.9846 | 1151.9598 | 1174.6565 | 1205.5051 | 1228.7382 | 1261.0568 | 1290.0158 | 1318.7363
| 16 | 1104.5 | 1143.7067 | 1155.7543 | 1177.2968 | 1197.2848 | 1217.8677 | 1235.1805 | 1258.0378 | 1272.3209 | 1301.0478 | 1325.9125 | 1350.6268
| 17 | 1139.3 | 1176.0453 | 1190.0023 | 1213.8687 | 1235.9761 | 1255.9131 | 1273.1063 | 1295.5794 | 1308.2305 | 1338.2148 | 1364.2229 | 1390.0529
| 18 | 1091.1 | 1140.8106 | 1156.7854 | 1182.6366 | 1206.3927 | 1224.9396 | 1241.9917 | 1263.7965 | 1274.3481 | 1304.8892 | 1331.6778 | 1358.1193
| 19 | 1038.2 | 1091.3371 | 1107.8952 | 1134.2134 | 1158.5298 | 1177.8332 | 1196.5159 | 1219.245 | 1231.0935 | 1262.7736 | 1290.8273 | 1318.481
| 20 | 990.5 | 1025.3268 | 1042.8584 | 1070.3242 | 1097.4577 | 1124.6297 | 1150.5207 | 1183.397 | 1207.4323 | 1245.9418 | 1281.2283 | 1316.1419
| 21 | 919.6 | 934.2915 | 950.5697 | 976.2413 | 1002.4681 | 1030.1454 | 1056.8157 | 1091.6063 | 1118.4001 | 1156.6742 | 1192.0617 | 1226.9722
| 22 | 828.5 | 824.8099 | 839.2418 | 863.2339 | 888.189 | 915.8743 | 943.6263 | 979.7389 | 1009.1992 | 1046.8092 | 1081.8632 | 1116.5711
| 23 | 735.5 | 730.4014 | 742.6997 | 765.0399 | 788.4171 | 816.3961 | 844.9723 | 882.4447 | 914.768 | 951.6599 | 986.2347 | 1020.5648

## Demand - AI
Demand Forecast for All-Island
4.4 The combined all-island forecast
Figure 4.22 Combined TER forecast for all-island system
| Year | Historical (TWh) | Low (TWh)* | Median (TWh)* | High (TWh)* | AIRAA24 (TWh)
| 2020 | 38.9
| 2021 | 40.3
| 2022 | 41.7
| 2023 | 42.13
| 2024 | 43.36 | 43.36 | 43.36 | 43.36 | 44.1
| 2025 |  | 44.47 | 45.38 | 46.25 | 46.1
| 2026 |  | 45.32 | 47.26 | 49.1 | 48.1
| 2027 |  | 46.25 | 49.09 | 51.81 | 50.2
| 2028 |  | 47.05 | 50.64 | 54.06 | 51.7
| 2029 |  | 47.85 | 52.18 | 56.26 | 53.1
| 2030 |  | 48.64 | 53.72 | 58.36 | 54.5
| 2031 |  | 49.42 | 55.21 | 60.23 | 56.1
| 2032 |  | 50.14 | 56.57 | 61.89 | 57.7
| 2033 |  | 50.85 | 57.81 | 63.3 | 59.1
| 2034 |  | 51.52 | 58.92 | 64.49 | 60.5
| 2035 |  | 52.19 | 59.9 | 65.58
* AIRAA25 Low, Median, High data for year 2024 is based on historic data for charting purposes, forecast begins in year 2025.
Figure 4.23 TER peak for the combined all-island forecast
| Year | Historical (MW) | Low (MW)* | Med (MW)* | High (MW)* | AIRAA24 (MW)
| 2020 | 6983
| 2021 | 7120
| 2022 | 7017
| 2023 | 7357
| 2024 | 7679 | 7679 | 7679 | 7679 | 7538
| 2025 |  | 7614 | 7762 | 7902 | 7720
| 2026 |  | 7639 | 7915 | 8183 | 7974
| 2027 |  | 7717 | 8089 | 8452 | 8190
| 2028 |  | 7779 | 8244 | 8699 | 8327
| 2029 |  | 7853 | 8401 | 8924 | 8449
| 2030 |  | 7918 | 8521 | 9110 | 8530
| 2031 |  | 7969 | 8675 | 9283 | 8662
| 2032 |  | 8034 | 8808 | 9444 | 8787
| 2033 |  | 8089 | 8917 | 9584 | 8901
| 2034 |  | 8140 | 9012 | 9721 | 9029
| 2035 |  | 8198 | 9115 | 9831
* AIRAA25 Low, Median, High data for year 2024 is based on historic data for charting purposes, forecast begins in year 2025.

## Generation - All Island
Generation - All Island
5.1 Introduction
Figure 5.1 Age breakdown of dispatchable conventional and hydro generation resources for the All-Island system operational from the start of 2026
| Conventional |  |  | Hydro
| Year | Capacity (MW) |  | Year | Capacity (MW)
| < 10 years | 1093 |  | < 10 years | 0
| 10 - 19 years | 2395 |  | 10 - 19 years | 292
| 20 - 29 years | 2708 |  | 20 - 79 years | 92
| > 29 years | 497 |  | > 79 years | 124
5.4.1 North South Tie Line
Table 5.5 North South Net Transfer Capacity
| N > S Capacity (MW) | S > N Capacity (MW) | Description
| 300 | 300 | Existing North South tie line. Included in all years of the study horizon for the jurisdictional central adequacy assessments.
| 900 | 950 | New North South Interconnector. Included from 2032 for the All-Island assessment.
5.4.2 HVDC interconnection from the all-island system to Great Britain and France
Table 5.6 HVDC Net Transfer Capacity (MW) assumptions for Northern Ireland/Ireland connection. Loss factors derived from Transmission Loss Adjustment Factors (TLAFs) for 2024-2025. The loss factor for Celtic is an anticipated loss factor based on engineering judgement of the EirGrid Interconnection team.
| Line | Import (MW) | Loss Factor | Comment
| Moyle | 450 | 2.4% | Increases to +/- 500 MW from 2028
| EWIC | 500 | 4.7%
| Greenlink | 500 | 2.3%
| Celtic | 700 | 4.2% | Assumed available from the start of Q2 2028
5.4.3 Further interconnection
Table 5.7 Further interconnection projects
| Project | Description | Project Promoters Target Commissioning Year | Assumed Net Transfer Capacity (MW)
| LirIC | Interconnector between Northern Ireland and Scotland | 2032 | 700
| MARES Connect | Interconnector between Ireland and Wales | 2029 | 750

## Generation - Conventional IE
Conventional Generation - IE
5.3.1. Ireland Portfolio
Table 5.1 Assumptions for conventional plant changes in Ireland
| Plant | Units | Capacity (MW) | Comment
| Moneypoint | MP1 | 250 | Following submission of a closure notice, these units exited the market at the end of June 2025. EirGrid notes that these units will be retained beyond this date to proactively mitigate the risks of an electricity crisis as defined by Regulation (EU) 2019/941 and the Risk Preparedness Plan (RPP) for Ireland. However, this is considered a mitigating measure and not part of the central assessment.
|  | MP2 | 250
|  | MP3 | 250
| Edenderry | ED3 | 58 | Awarded capacity in the 2025/2026 T-4 capacity auction to switch fuel from Distillate Oil to Gas.
|  | ED5 | 58
| FlexGen | Ringsend | 64 | Newly operational as of Q4 2024.
|  | Poolbeg | 64
|  | Corduff | 64
Table 5.2 Ireland assumptions for new conventional plant capacities in adequacy studies (rated MW)
| Cumulative (MW) | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Total Successful in Capacity Auctions less Operational Plant | 900 | 2060 | 2110 | 2450 | 2450 | 2450 | 2450 | 2450 | 2450 | 2450
| AIRAA 2025 Expected New Capacity Delivery | 610 | 910 | 1500 | 1900 | 1900 | 1900 | 1900 | 1900 | 1900 | 1900
Table 5.3 Capacity (MW) assumed to be subject to run hour limits in Ireland
| Run Hour Restriction | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| 500 hours | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270
| 1500 hours | 210 | 210 | 510 | 510 | 510 | 510 | 510 | 510 | 510 | 510

## Generation - Conventional NI
Conventional Generation - NI
5.3.2 Northern Ireland Portfolio
Table 5.4 Capacity (MW) assumed to be subject to run hour limits in Northern Ireland
| Run Hour Restriction | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| 500 hours | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310
| 1500 hours | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700

## Generation - Renewable IE
Renewable Generation - IE
5.5.1 Ireland Portfolio
Table 5.8 Climate Action Plan renewable targets in Ireland
| Technology | 2025 Target | 2030 Target
| Onshore Wind | 6 GW | 9 GW
| Offshore Wind | - | At least 5 GW
| Solar | Up to 5 GW | 8 GW
Figure 5.2 Assumed growth of variable generation capacity in Ireland
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Onshore Wind | 5.744 | 6.068 | 6.441 | 6.811 | 7.13 | 7.533 | 7.939 | 8.35 | 8.77 | 9.189
| Solar PV | 3.261 | 4.014 | 4.768 | 5.521 | 6.279 | 6.883 | 7.476 | 8.061 | 8.639 | 9.222
| Offshore Wind | 0.025 | 0.025 | 0.025 | 0.025 | 1.354 | 1.952 | 2.516 | 3.118 | 3.727 | 4.481
*The AIRAA median variable generation forecast is aligned with the Sustainable Energy Authority of Ireland's
Decarbonised Electricity System Study (DESS) - Forecasts of plausible rates of generation technology
deployment 2024-2040 EPO50 forecast for Solar PV, Onshore Wind and Offshore Wind.
Decarbonised electricity system study ¦ Renewable Energy ¦ SEAI

## Generation - Renewable NI
Renewable Generation - NI
5.5.2 Northern Ireland Portfolio
Figure 5.3 Assumed growth of renewable capacity in Northern Ireland
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Onshore Wind | 1.41 | 1.47 | 1.55 | 1.7 | 1.85 | 2 | 2.15 | 2.3 | 2.45 | 2.6
| Solar PV | 0.27 | 0.3 | 0.35 | 0.41 | 0.48 | 0.55 | 0.62 | 0.69 | 0.76 | 0.83
| Offshore Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5

## Generation - Non-Conventional
Non-Conventional Generation
5.6.1 Ireland Portfolio
Table 5.9 Ireland energy storage capacity (MW) rounded to the nearest 10 MW
| Duration | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| <= 1 Hour | 460 | 460 | 460 | 480 | 480 | 480 | 480 | 480 | 480 | 480
| 1-4 Hours | 390 | 530 | 620 | 920 | 920 | 920 | 920 | 920 | 920 | 920
| > 4 Hours | 0 | 0 | 0 | 110 | 110 | 110 | 110 | 110 | 110 | 110
| Pump Storage | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290
| Total | 1140 | 1280 | 1370 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800
Table 5.10 Ireland energy storage (MWh) rounded to the nearest 10 MWh
| Duration | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| <= 1 Hour | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290
| 1-4 Hours | 880 | 1390 | 1510 | 2220 | 2220 | 2220 | 2220 | 2220 | 2220 | 2220
| > 4 Hours | 0 | 0 | 0 | 650 | 650 | 650 | 650 | 650 | 650 | 650
| Pump Storage | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600 | 1600
| Total | 2770 | 3280 | 3400 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760
5.6.2 Northern Ireland Portfolio
Table 5.11 Northern Ireland energy storage capacity (MW) rounded to the nearest 10 MW
| Duration | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| <= 1 Hour | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
| 1-4 Hours | 10 | 10 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 40
| Total | 210 | 210 | 220 | 240 | 240 | 240 | 240 | 240 | 240 | 240
Table 5.12 Northern Ireland energy storage (MWh) rounded to the nearest 10 MWh
| Duration | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| <= 1 Hour | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140
| 1-4 Hours | 20 | 20 | 50 | 80 | 80 | 80 | 80 | 80 | 80 | 80
| Total | 160 | 160 | 190 | 220 | 220 | 220 | 220 | 220 | 220 | 220
5.7.1 Ireland Portfolio
Table 5.13 Ireland DSU capacity (MW) rounded to the nearest 10 MW
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Run Hour Limited | 570 | 520 | 570 | 750 | 750 | 750 | 750 | 750 | 750 | 750
| Non-Run Hour Limited | 190 | 230 | 290 | 480 | 480 | 480 | 480 | 480 | 480 | 480
Table 5.14 Ireland DSU run hour restriction (hours)
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Daily Activation Limit | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
5.7.2 Northern Ireland Portfolio
Table 5.15 Northern Ireland DSU capacity (MW) rounded to the nearest 10 MW
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Run Hour Limited | 140 | 80 | 120 | 130 | 130 | 130 | 130 | 130 | 130 | 130
| Non-Run Hour Limited | 50 | 50 | 60 | 110 | 110 | 110 | 110 | 110 | 110 | 110
Table 5.16 Northern Ireland DSU run hour restriction (hours)
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Daily Activation Limit | 3 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Table 5.17 Northern Ireland AGU capacity (MW)
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| AGU | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79

## Generation - Availability
Generation Plant Availability
5.9 Plant Availability
Table 5.18 Summary of technology class availability statistics
| Technology Category | Mean Forced Outage Probability (%) | Mean Scheduled Outage Rate (%) | Mean Scheduled Outage Duration (hours) | Annual Availability (%)
| DSU | * | * | * | 26.2
| DSU Run Hour Limited | * | * | * | 23.4
| Gas Turbine | 11.1 | 4.8 | 420 | 84.1
| Hydro | 13.4 | 5.9 | 520 | 80.7
| Steam Turbine | 15.9 | 7.6 | 660 | 76.5
| Interconnector | 4.5 | 3.8 | 340 | 91.7
| Pumped Hydro Storage | 2.7 | 5.2 | 450 | 92.1
| Other Storage*** | 5.1 | ** | ** | 94.9
| System Wide | 21.1 | 6.1 | 540 | 72.7
* In line with the monthly availability reporting, availability of DSUs considers a capacity-weighted availability instead of forced and scheduled outage statistics.
** Scheduled outages for battery storage units were observed to be close to 0% and therefore have not been included as part of this assessment.
*** Other Storage statistics are based on one year of availability data, which will be expanded on over the coming years as more data becomes available.
5.9.1 Historic plant availability
Figure 5.4 All-island average annual generation capacity availability for the past 10 years (excluding DSU)
| Year | Availability | 2024 5-Year Average | 2019 5-Year Average
| 2015 | 89.5 |  | 86.78
| 2016 | 89.7
| 2017 | 90.2
| 2018 | 84.7
| 2019 | 79.8
| 2020 | 81.1 | 76.32
| 2021 | 71.4
| 2022 | 74.4
| 2023 | 77.3
| 2024 | 77.4
Figure 5.5 Average annual conventional generation capacity forced and scheduled outage rates in Ireland for the past 10 years
| Year | Scheduled Outage Rate (IE) (%) | 2024 5-Year Average | 2019 5-Year Average |  | Year | Forced Outage Rate (IE) (%) | 2024 5-Year Average | 2019 5-Year Average
| 2015 | 4.9 |  | 6.28 |  | 2015 | 2.9 |  | 5.92
| 2016 | 5.7 |  |  |  | 2016 | 4.1
| 2017 | 3.4 |  |  |  | 2017 | 5.5
| 2018 | 8.1 |  |  |  | 2018 | 6.8
| 2019 | 9.3 |  |  |  | 2019 | 10.3
| 2020 | 5.8 | 5.24 |  |  | 2020 | 12.6 | 17.76
| 2021 | 7.8 |  |  |  | 2021 | 21.9
| 2022 | 6.5 |  |  |  | 2022 | 18.1
| 2023 | 3.1 |  |  |  | 2023 | 17.8
| 2024 | 3 |  |  |  | 2024 | 18.4
Figure 5.6 Average annual conventional generation capacity forced and scheduled outage rates in Northern Ireland for the past 10 years
| Year | Scheduled Outage Rate (IE) (%) | 2024 5-Year Average | 2019 5-Year Average |  | Year | Forced Outage Rate (IE) (%) | 2024 5-Year Average | 2019 5-Year Average
| 2015 | 4 |  | 3.76 |  | 2015 | 10.3 |  | 8.34
| 2016 | 4.4 |  |  |  | 2016 | 4.6
| 2017 | 1.1 |  |  |  | 2017 | 6.4
| 2018 | 1.5 |  |  |  | 2018 | 9.9
| 2019 | 7.8 |  |  |  | 2019 | 10.5
| 2020 | 6.2 | 6.04 |  |  | 2020 | 9.7 | 13.9
| 2021 | 8.7 |  |  |  | 2021 | 12.7
| 2022 | 8 |  |  |  | 2022 | 13.9
| 2023 | 4.7 |  |  |  | 2023 | 16.5
| 2024 | 2.6 |  |  |  | 2024 | 16.7
Figure 5.7 Ireland and Northern Ireland conventional generation capacity availability across the last 10 years
| Date | Ireland | Northern Ireland
| 2014-01-01 | 87.4106 | 89.6437
| 2014-02-01 | 86.9706 | 89.5818
| 2014-03-01 | 87.3456 | 88.5638
| 2014-04-01 | 87.1262 | 87.2384
| 2014-05-01 | 86.59 | 86.9698
| 2014-06-01 | 85.9043 | 87.216
| 2014-07-01 | 85.3719 | 87.5872
| 2014-08-01 | 85.3313 | 87.3543
| 2014-09-01 | 84.7814 | 86.2339
| 2014-10-01 | 84.2184 | 85.8895
| 2014-11-01 | 84.1348 | 85.7819
| 2014-12-01 | 85.138 | 85.0584
| 2015-01-01 | 86.3639 | 85.6
| 2015-02-01 | 86.9313 | 85.489
| 2015-03-01 | 87.6114 | 85.8782
| 2015-04-01 | 88.5203 | 86.2004
| 2015-05-01 | 89.5091 | 85.4349
| 2015-06-01 | 90.6502 | 85.3642
| 2015-07-01 | 91.1194 | 85.1724
| 2015-08-01 | 90.9593 | 84.8501
| 2015-09-01 | 91.511 | 84.7482
| 2015-10-01 | 92.2731 | 83.954
| 2015-11-01 | 91.8568 | 83.9377
| 2015-12-01 | 91.6963 | 84.0648
| 2016-01-01 | 91.5092 | 83.9652
| 2016-02-01 | 91.469 | 84.2295
| 2016-03-01 | 91.2074 | 84.962
| 2016-04-01 | 90.8919 | 86.0398
| 2016-05-01 | 90.6191 | 86.6182
| 2016-06-01 | 89.5453 | 86.2096
| 2016-07-01 | 89.7352 | 86.6565
| 2016-08-01 | 90.1774 | 86.6489
| 2016-09-01 | 90.2497 | 86.4056
| 2016-10-01 | 89.7966 | 87.3674
| 2016-11-01 | 90.368 | 88.2747
| 2016-12-01 | 90.0052 | 88.8274
| 2017-01-01 | 90.2413 | 88.4642
| 2017-02-01 | 90.1096 | 88.2439
| 2017-03-01 | 90.2463 | 88.2932
| 2017-04-01 | 90.2864 | 88.1859
| 2017-05-01 | 90.6362 | 88.6377
| 2017-06-01 | 91.2506 | 89.6891
| 2017-07-01 | 91.093 | 89.6217
| 2017-08-01 | 91.0197 | 90.315
| 2017-09-01 | 90.5103 | 90.5719
| 2017-10-01 | 90.5686 | 90.7769
| 2017-11-01 | 89.9365 | 90.698
| 2017-12-01 | 90.1541 | 90.4019
| 2018-01-01 | 89.943 | 90.8931
| 2018-02-01 | 89.5534 | 91.365
| 2018-03-01 | 88.9535 | 91.3749
| 2018-04-01 | 88.4437 | 90.9003
| 2018-05-01 | 88.0412 | 90.7543
| 2018-06-01 | 87.6867 | 89.5412
| 2018-07-01 | 87.5296 | 88.6745
| 2018-08-01 | 87.4208 | 87.7706
| 2018-09-01 | 87.9965 | 88.1567
| 2018-10-01 | 86.9049 | 87.7612
| 2018-11-01 | 85.9045 | 87.0248
| 2018-12-01 | 84.0721 | 86.6411
| 2019-01-01 | 82.3531 | 85.1516
| 2019-02-01 | 81.5589 | 83.9705
| 2019-03-01 | 80.7477 | 83.0359
| 2019-04-01 | 80.1777 | 82.1799
| 2019-05-01 | 79.6933 | 80.9664
| 2019-06-01 | 79.1679 | 80.8428
| 2019-07-01 | 78.5145 | 80.5854
| 2019-08-01 | 77.5933 | 80.0822
| 2019-09-01 | 76.6255 | 80.2454
| 2019-10-01 | 77.0196 | 80.6793
| 2019-11-01 | 78.2481 | 81.0417
| 2019-12-01 | 79.4302 | 81.1489
| 2020-01-01 | 80.441 | 81.824
| 2020-02-01 | 80.9039 | 82.1911
| 2020-03-01 | 81.2482 | 82.6305
| 2020-04-01 | 81.4834 | 83.7498
| 2020-05-01 | 81.8459 | 84.7787
| 2020-06-01 | 82.047 | 85.7416
| 2020-07-01 | 81.9002 | 86.3933
| 2020-08-01 | 81.8655 | 86.0752
| 2020-09-01 | 81.8774 | 85.6609
| 2020-10-01 | 81.6572 | 83.9092
| 2020-11-01 | 81.2616 | 82.235
| 2020-12-01 | 80.6556 | 82.5914
| 2021-01-01 | 80.2008 | 82.9102
| 2021-02-01 | 79.0074 | 82.821
| 2021-03-01 | 78.2546 | 82.4517
| 2021-04-01 | 77.0244 | 82.0896
| 2021-05-01 | 75.03 | 81.2877
| 2021-06-01 | 73.6099 | 79.7651
| 2021-07-01 | 72.3371 | 79.0364
| 2021-08-01 | 71.4129 | 79.956
| 2021-09-01 | 70.0051 | 79.0889
| 2021-10-01 | 69.3956 | 79.1568
| 2021-11-01 | 68.7968 | 79.3701
| 2021-12-01 | 69.4139 | 78.4462
| 2022-01-01 | 69.9054 | 78.0907
| 2022-02-01 | 70.984 | 78.1604
| 2022-03-01 | 71.1495 | 78.5925
| 2022-04-01 | 71.5807 | 77.8883
| 2022-05-01 | 72.0374 | 77.1539
| 2022-06-01 | 72.4127 | 77.3757
| 2022-07-01 | 72.8021 | 76.8017
| 2022-08-01 | 73.2503 | 75.164
| 2022-09-01 | 74.1702 | 75.0891
| 2022-10-01 | 74.1344 | 75.27
| 2022-11-01 | 74.2666 | 75.3662
| 2022-12-01 | 74.1718 | 75.4126
| 2023-01-01 | 73.9147 | 75.1647
| 2023-02-01 | 73.6064 | 74.9137
| 2023-03-01 | 73.784 | 74.3792
| 2023-04-01 | 74.2467 | 74.8907
| 2023-05-01 | 74.9315 | 74.2102
| 2023-06-01 | 75.2174 | 73.5966
| 2023-07-01 | 75.578 | 73.1578
| 2023-08-01 | 75.8854 | 72.9162
| 2023-09-01 | 75.7464 | 73.1968
| 2023-10-01 | 76.6001 | 74.6067
| 2023-11-01 | 77.3227 | 76.0047
| 2023-12-01 | 77.6838 | 76.9065
| 2024-01-01 | 77.8495 | 77.8618
| 2024-02-01 | 77.7653 | 78.6121
| 2024-03-01 | 77.9304 | 79.511
| 2024-04-01 | 78.0433 | 80.2484
| 2024-05-01 | 77.75 | 82.4498
| 2024-06-01 | 77.7556 | 83.8546
| 2024-07-01 | 77.5901 | 85.1308
| 2024-08-01 | 77.8247 | 85.3096
| 2024-09-01 | 77.9621 | 83.826
| 2024-10-01 | 77.8511 | 82.2462
| 2024-11-01 | 77.5345 | 81.6393
| 2024-12-01 | 77.1217 | 80.1851
| 2025-01-01 | 77.1217 | 80.1851
Figure 5.8 All-Island demand side unit monthly availability for 2022 to 2025 calendar years
| Year | DSU Monthly Availability | DSU MW Capacity (Rated)
| 2022-01-01 | 161.6 | 726.4
| 2022-02-01 | 185.7 | 726.4
| 2022-03-01 | 176.9 | 729.4
| 2022-04-01 | 197.4 | 749.4
| 2022-05-01 | 195.9 | 747.4
| 2022-06-01 | 197.4 | 750.4
| 2022-07-01 | 156.4 | 750.4
| 2022-08-01 | 160.8 | 751.4
| 2022-09-01 | 182.8 | 745.4
| 2022-10-01 | 184.2 | 752.4
| 2022-11-01 | 184.2 | 761.4
| 2022-12-01 | 145.5 | 752.4
| 2023-01-01 | 159.4 | 752.4
| 2023-02-01 | 170.3 | 752.4
| 2023-03-01 | 184.2 | 730.8
| 2023-04-01 | 166.7 | 752.4
| 2023-05-01 | 198.8 | 730.8
| 2023-06-01 | 186.4 | 750.4
| 2023-07-01 | 187.1 | 730.8
| 2023-08-01 | 167.4 | 772.4
| 2023-09-01 | 177.6 | 721.8
| 2023-10-01 | 162.3 | 754.4
| 2023-11-01 | 138.2 | 751.4
| 2023-12-01 | 131.6 | 751.4
| 2024-01-01 | 132.3 | 818.2
| 2024-02-01 | 162.3 | 814.2
| 2024-03-01 | 156.4 | 819.2
| 2024-04-01 | 168.1 | 816.2
| 2024-05-01 | 175.4 | 845.2
| 2024-06-01 | 172.5 | 841.8
| 2024-07-01 | 176.9 | 842
| 2024-08-01 | 169.6 | 842
| 2024-09-01 | 169.6 | 861.2
| 2024-10-01 | 166.7 | 847.4
| 2024-11-01 | 167.4 | 850.4
| 2024-12-01 | 138.2 | 851.4
| 2025-01-01 | 138.2 | 851.4

## Adequacy
Adequacy
6.1 Introduction
Table 6.1 LOLE Reliability Standards
| Area | LOLE Reliability Standard (hours)
| All-Island SEM | 6.5
| Ireland | 3
| Northern Ireland | 4.9
6.4 Ireland adequacy analysis
Figure 6.2 Base and Secure Loss of Load Expectation Results for Ireland
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| LOLE Base | 71.6 | 43.6 | 7.9 | 1.5 | 0.4 | 0.3 | 0.4 | 0.7 | 0.9 | 1.6
| LOLE Secure | 88.5 | 57 | 14.6 | 4.1 | 3.1 | 2.8 | 3 | 4.1 | 7.1 | 5.4
| 3 hour Reliability Standard | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Table 6.2 LOLE and EENS Base results for Ireland (includes reserves)
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| LOLE Base (hours) | 71.6 | 43.6 | 7.9 | 1.5 | 0.4 | 0.3 | 0.4 | 0.7 | 0.9 | 1.6
| EENS Base (GWh) | 23.9 | 14.1 | 2.5 | 0.5 | 0.1 | 0.1 | 0.1 | 0.2 | 0.2 | 0.4
Table 6.3 LOLE and EENS Base Demand Only results for Ireland (excludes reserves)
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| LOLE Base Demand Only (hours) | 28.3 | 16.9 | 2.1 | 0.3 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3
| EENS Base Demand Only (GWh) | 8.6 | 4.9 | 0.6 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0.1
Table 6.4 Average LOLE of the 3 weather scenarios used in the surplus/deficit calculation for Ireland (includes reserves)
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| 3 weather scenario LOLE | 77 | 45.6 | 6.7 | 1.6 | 0.4 | 0.4 | 0.5 | 0.6 | 0.8 | 2
Figure 6.3 MW Base results for Ireland in terms of surplus (+) and deficit (-) of perfect plant
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Demand | -635 | -395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reserve | -375 | -375 | -220 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MW Base | -1010 | -770 | -220 | 200 | 640 | 550 | 530 | 410 | 420 | 160
Table 6.5 LOLE and EENS Secure results for Ireland (includes reserves)
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| LOLE Secure (hours) | 88.5 | 57 | 14.6 | 4.1 | 3.1 | 2.8 | 3 | 4.1 | 7.1 | 5.4
| EENS Secure (GWh) | 32.1 | 19.5 | 5.6 | 1.3 | 1 | 0.9 | 0.9 | 1.2 | 2.6 | 1.8
Figure 6.4 Secure surplus/deficit results for Ireland in terms of surplus (+) and deficit (-) of perfect plant
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Demand | -695 | -495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reserve | -375 | -375 | -380 | 0 | 0 | 0 | 0 | 0 | -90 | -70
| TOPs | -350 | -350 | -350 | -260 | -150 | 0 | -170 | -250 | -350 | -350
| MW Secure | -1420 | -1220 | -730 | -260 | -150 | 0 | -170 | -250 | -440 | -420
Figure 6.5 Sensitivity analysis for Ireland
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Low Demand | 250 | 320 | 430 | 450 | 510 | 610 | 680 | 780 | 820 | 850
| High Demand | -240 | -320 | -370 | -410 | -500 | -510 | -590 | -650 | -660 | -690
| Low RES | -60 | -90 | -100 | -100 | -350 | -370 | -310 | -260 | -270 | -290
| High RES | 50 | 40 | 150 | 340 | 220 | 250 | 230 | 210 | 210 | 270
| Energy Storage |  |  |  |  | 210 | 260 | 180 | 240 | 200 | 320
| CM Gas Delivery | 480 | 1010 | 660 | 720 | 460 | 460 | 460 | 430 | 370 | 460
| Low Flex | -70 | -120 | -140 | -200 | -240 | -230 | -250 | -180 | -230 | -160
| High Flex | 60 | 40 | 30 | 100 | 100 | 130 | 160 | 210 | 160 | 320
| New Technology Load Sensitivity | -100 | -150 | -220 | -280 | -340 | -460 | -590 | -730 | -920 | -1100
Table 6.6 Low RES renewable trajectory (MW)
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Offshore Wind | 30 | 30 | 30 | 30 | 30 | 30 | 400 | 830 | 980 | 1010
| Onshore Wind | 5390 | 5600 | 5810 | 6020 | 6200 | 6490 | 6790 | 7100 | 7360 | 7610
| Solar | 2220 | 2620 | 3030 | 3430 | 3840 | 4220 | 4600 | 4980 | 5370 | 5440
Table 6.7 High RES renewable trajectory (MW)
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Offshore Wind | 30 | 30 | 410 | 1340 | 3650 | 4430 | 5200 | 6020 | 6870 | 7730
| Onshore Wind | 6400 | 6940 | 7470 | 8010 | 8460 | 9020 | 9580 | 10130 | 10680 | 11220
| Solar | 4120 | 5160 | 6200 | 7230 | 8270 | 9010 | 9830 | 10670 | 11580 | 12490
Table 6.8 Ireland high storage additional capacity
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Capacity (MW) | 0 | 0 | 0 | 0 | 650 | 800 | 800 | 800 | 800 | 800
| Storage (MWh) | 0 | 0 | 0 | 0 | 2450 | 2900 | 2900 | 2900 | 2900 | 2900
Figure 6.6 Ireland adequacy position with mitigating measures
|  | 2026 |  | 2027 |  | 2028 |  | 2029 | 2030
| Demand | 2026: -695; 2028: -495; 2030: 0; 2032: 0; 2033: 0
| Reserve | 2026: -375; 2028: -375; 2030: -380; 2032: 0; 2033: 0
| TOPs | 2026: -350; 2028: -350; 2030: -350; 2032: -260; 2033: -150
| MW Secure | 2026: -1420; 2028: -1220; 2030: -730; 2032: -260; 2033: -150
| Confirmed SoS Measures | 2027: -1170; 2029: -520; 2031: -520
| Possible SoS Measures | 2029: -650; 2031: -410
6.5 Northern Ireland adequacy analysis
Figure 6.7 Base and Secure Loss of Load expectation results for Northern Ireland
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| LOLE Base | 3.7 | 4 | 2.9 | 4.1 | 3.4 | 4.7 | 5.5 | 7.3 | 11.2 | 11.3
| LOLE Secure | 16.1 | 14.7 | 10 | 14.4 | 17.2 | 20.8 | 24.8 | 35.4 | 48.2 | 43.6
| 4.9 hour Reliability Standard | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9
Table 6.9 LOLE and EENS Base results for Northern Ireland (includes reserves)
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| LOLE Base (hours) | 3.7 | 4 | 2.9 | 4.1 | 3.4 | 4.7 | 5.5 | 7.3 | 11.2 | 11.3
| EENS Base (GWh) | 0.5 | 0.5 | 0.3 | 0.5 | 0.4 | 0.5 | 0.6 | 1 | 1.4 | 1.6
Table 6.10 LOLE and EENS base demand only results for Northern Ireland (excludes reserves)
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| LOLE Base Demand Only (hours) | 1.5 | 1.7 | 0.8 | 1.2 | 0.9 | 1.3 | 1.4 | 2.2 | 3.5 | 4
| EENS Base Demand Only (GWh) | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.3 | 0.4 | 0.5
Table 6.11 Average LOLE of the 3 weather scenarios used in the surplus/deficit calculation for Northern Ireland (includes reserves)
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| 3 weather scenario LOLE | 4.2 | 4.9 | 2.6 | 4 | 3.9 | 4.6 | 6.4 | 8.7 | 13.1 | 12.7
Figure 6.8 MW base results for Northern Ireland in terms of surplus (+) and deficit (-) of perfect plant
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reserve | 0 | 0 | 0 | 0 | 0 | 0 | -30 | -70 | -110 | -120
| MW Base | 20 | 10 | 70 | 30 | 30 | 10 | -30 | -70 | -110 | -120
Table 6.12 LOLE and EENS Secure results for Northern Ireland (includes reserves)
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| LOLE Secure (hours) | 16.1 | 14.7 | 10 | 14.4 | 17.2 | 20.8 | 24.8 | 35.4 | 48.2 | 43.6
| EENS Secure (GWh) | 2.2 | 2 | 1.3 | 1.8 | 2.2 | 2.6 | 3.2 | 5 | 7.2 | 6.5
Figure 6.9 MW secure results for Northern Ireland in terms of surplus (+) and deficit (-) of perfect plant
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Demand | -85 | -35 | 0 | 0 | 0 | -25 | -25 | -135 | -115 | -145
| Reserve | -125 | -125 | -80 | -140 | -160 | -175 | -175 | -175 | -175 | -175
| MW Secure | -210 | -160 | -80 | -140 | -160 | -200 | -200 | -310 | -290 | -320
Figure 6.10 Sensitivity analysis for Northern Ireland
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Low Demand | 40 | 50 | 60 | 60 | 70 | 90 | 80 | 90 | 110 | 110
| High Demand | -50 | -70 | -60 | -80 | -90 | -90 | -110 | -120 | -130 | -140
| Low RES | 0 | 0 | -10 | -20 | -20 | -20 | -30 | -40 | -20 | -70
| High RES | 0 | 0 | 0 | 0 | 50 | 70 | 50 | 60 | 60 | 30
| High Storage | 0 | 30 | 50 | 80 | 90 | 150 | 90 | 120 | 130 | 120
| Low Flex |  |  |  |  | -30 | -10 | -50 | -40 | -30 | -50
| High Flex | 10 | 10 | 30 | 40 | 20 | 50 | 30 | 50 | 70 | 80
| Low ARHL Avail | -30 | -30 | -20 | -20 | -50 | -30 | -60 | -40 | -30 | -30
| No ARHL | 260 | 240 | 260 | 270 | 280 | 280 | 260 | 320 | 300 | 320
Table 6.13 Northern Ireland low renewable trajectory (MW)
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Offshore Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Onshore Wind | 1395 | 1425 | 1465 | 1540 | 1615 | 1690 | 1765 | 1840 | 1915 | 1990
| Solar | 260 | 275 | 300 | 330 | 365 | 400 | 435 | 470 | 505 | 540
Table 6.14 Northern Ireland high renewable trajectory (MW)
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Offshore Wind | 0 | 0 | 0 | 0 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
| Onshore Wind | 1420 | 1490 | 1590 | 1780 | 1970 | 2160 | 2340 | 2530 | 2720 | 2910
| Solar | 280 | 310 | 380 | 450 | 540 | 630 | 710 | 800 | 890 | 980
Table 6.15 Northern Ireland high storage additional capacity
|  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Capacity (MW) | 0 | 100 | 150 | 280 | 530 | 720 | 720 | 720 | 720 | 720
| Storage (MWh) | 0 | 200 | 250 | 500 | 950 | 1420 | 1420 | 1420 | 1420 | 1420
6.6 All-island adequacy analysis
Table 6.16 Base results for the All-Island system
|  | 2032 | 2033 | 2034 | 2035
| LOLE Base (hours) | 2026: 0.2; 2027: 0.1; 2028: 0.3; 2029: 0.4
| EENS Base (GWh) | 2026: 0; 2027: 0; 2028: 0.1; 2029: 0.1
| MW Base | 2026: 1010; 2027: 1020; 2028: 1020; 2029: 8,30
Table 6.17 Secure results for the All-Island system
|  | 2032 | 2033 | 2034 | 2035
| LOLE Secure (hours) | 2026: 1.2; 2027: 1.4; 2028: 4; 2029: 2.6
| EENS Secure (GWh) | 2026: 0; 2027: 0.2; 2028: 1.1; 2029: 0.3
| MW Secure | 2026: 360; 2027: 340; 2028: -30; 2029: 80
Figure 6.11 MW results for the All-Island in terms of surplus (+) and deficit (-) of perfect plant
|  | 2032 | 2033 | 2034 | 2035
| MW Base | 2026: 1010; 2027: 1020; 2028: 1020; 2029: 830
| MW Secure | 2026: 360; 2027: 340; 2028: -30; 2029: 80

## Appendix 1
Appendix 1: Economic Viability Assessment
Table A1.1 EVA considerations
| Number | Comment
| 1 | The EVA does not model system operational or transmission constraints (e.g. inertia, must-run, SNSP, transmission), which may misrepresent actual revenue potential for some units.
| 2 | The EVA adopts a simplified view of costs and revenues which do not take into account all considerations taken as part of a financial assessment for a project. Therefore, the EVA outputs simplify “viability” and do not aim to predict how investors would make decisions.
| 3 | The model is limited to a 10-year horizon and therefore modelling of costs and revenues beyond 2035 has not been conducted, instead values from the last modelled year are retained for the remainder of the unit’s lifetime.
| 4 | The EVA outcome relies heavily on inputs which are uncertain including fuel prices, technology costs, renewable trajectory, demand trajectory and changes in neighbouring regions (e.g. Great Britain and France).
| 5 | The EVA does not model future capacity market auctions. This assumption is to provide a perspective on viability without capacity market support and is not a comment on the likelihood of future capacity auctions.
| 6 | Renewable capacities are not included in the EVA as they are assumed to be driven by policy support schemes.
| 7 | The entry and exit of Demand Side Units (DSU) has not been considered due to lack of data regarding costs and other inputs.
| 8 | A single weather scenario (WS) has been selected as a representative WS; in reality the outturn climate conditions could have a material effect on the viability of units for a given study year.
| 9 | The source used for the cost assumptions is the SEMC BNE study which may be outdated and may underestimate actual costs. Additionally, the categories used are for CCGTs and OCGTs and these are not broken down by the age of the unit or specific types of CCGTs and OCGTs.
Table A1.2 Economic Viability Assessment (EVA) summary of scenarios
| Scenario | Implementation | Rationale
| S1 - With scarcity pricing | The price cap in the economic dispatch has been fixed to the values used in ERAA 2024. | Assessment price cap assumption aligned with ERAA 2024.
| S2 - Without scarcity pricing | Prices in the economic dispatch are capped at 500 €/MWh. | Consultation feedback that historic SEM prices have rarely exceed 500 €/MWh, otherwise aligned with Scenario 1.
| S3 – Energy only revenue | Only energy revenues are included as part of the assessment. | Consultation feedback that there is uncertainty regarding future ancillary service revenue, otherwise aligned with Scenario 1.
| S4 - Low battery costs | Battery capex and opex is 30% lower, with the economic lifetime of batteries increased from 10 to 20 years. | Assess impact of lower storage costs and test ability of EVA process to commission new resources, otherwise aligned with Scenario 1.
| S5 – Without scarcity pricing & energy only revenue | Revenues from the economic dispatch are capped at 500 €/MWh, only energy revenues are included, and the highest revenue monte carlo sample from each weather scenario is excluded. | A look at “stacking” multiple aspects of consultation feedback including S2, S3.
Figure A1.2 Economic Viability Assessment (EVA) rated capacity changes compared to the central adequacy scenario
| Scenario | Category | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| S1 - with scarcity pricing | Gas Turbine | -950 | -950 | -950 | -950 | -1140 | -1340
|  | Batteries | 0 | 0 | 0 | 0 | 0 | 0
|  | Net Position | -950 | -950 | -950 | -950 | -1140 | -1340
| S2 - without scarcity pricing | Gas Turbine | -950 | -950 | -950 | -950 | -1490 | -1720
|  | Batteries | 0 | 0 | 0 | 0 | 0 | 0
|  | Net Position | -950 | -950 | -950 | -950 | -1490 | -1720
| S3 - Energy only revenue | Gas Turbine | -1400 | -1400 | -1400 | -1400 | -1590 | -1730
|  | Batteries | 0 | 0 | 0 | 0 | 0 | 0
|  | Net Position | -1400 | -1400 | -1400 | -1400 | -1590 | -1730
| S4 - low battery costs | Gas Turbine | -950 | -950 | -950 | -950 | -1490 | -1660
|  | Batteries | 100 | 220 | 400 | 700 | 1200 | 1950
|  | Net Position | -850 | -730 | -550 | -250 | -290 | 290
| S5 - Without scarcity pricing & energy only revenue | Gas Turbine | -1410 | -1410 | -1410 | -1410 | -2310 | -2410
|  | Batteries | 0 | 0 | 0 | 0 | 0 | 0
|  | Net Position | -1410 | -1410 | -1410 | -1410 | -2310 | -2410

## Appendix 2
Appendix 2: Demand Scenarios
Table A2.1 Demand forecast for the median scenario in calendar year format for Ireland and Northern Ireland
| Median | Calendar Year TER (TWh) | [5 empty] | TER Peak (GW) |  |  | Transmission Peak (GW)
| Year | Ireland |  | Northern Ireland |  | All-Island |  | Ireland | Northern Ireland | All-Island | Ireland | Northern Ireland | All-Island
|  | TER (TWh) | % Growth | TER (TWh) | % Growth | TER (TWh) | % Growth
| 2024 | 35.2 | 3.8% | 8.2 | 0.6% | 43.4 | 3.2% | 6.02 | 1.66 | 7.63 | 5.91 | 1.61 | 7.48
| 2025 | 37.2 | 5.7% | 8.2 | 0.4% | 45.4 | 4.7% | 6.16 | 1.63 | 7.76 | 6.04 | 1.59 | 7.61
| 2026 | 39 | 4.8% | 8.3 | 1.3% | 47.3 | 4.1% | 6.29 | 1.65 | 7.92 | 6.17 | 1.61 | 7.76
| 2027 | 40.6 | 4.2% | 8.5 | 2.4% | 49.1 | 3.9% | 6.42 | 1.69 | 8.09 | 6.31 | 1.65 | 7.94
| 2028 | 41.9 | 3.3% | 8.7 | 2.4% | 50.6 | 3.2% | 6.55 | 1.73 | 8.24 | 6.43 | 1.69 | 8.09
| 2029 | 43.3 | 3.1% | 8.9 | 2.6% | 52.2 | 3.1% | 6.67 | 1.76 | 8.4 | 6.56 | 1.72 | 8.25
| 2030 | 44.6 | 3% | 9.2 | 2.6% | 53.7 | 2.9% | 6.79 | 1.79 | 8.52 | 6.68 | 1.75 | 8.37
| 2031 | 45.7 | 2.6% | 9.5 | 3.5% | 55.2 | 2.8% | 6.9 | 1.85 | 8.68 | 6.79 | 1.81 | 8.53
| 2032 | 46.8 | 2.3% | 9.8 | 3.3% | 56.6 | 2.5% | 6.99 | 1.9 | 8.81 | 6.88 | 1.86 | 8.66
| 2033 | 47.7 | 2% | 10.1 | 3.1% | 57.8 | 2.2% | 7.07 | 1.96 | 8.92 | 6.96 | 1.92 | 8.77
| 2034 | 48.5 | 1.7% | 10.4 | 2.9% | 58.9 | 1.9% | 7.14 | 2.01 | 9.01 | 7.03 | 1.97 | 8.86
| 2035 | 49.2 | 1.4% | 10.7 | 2.8% | 59.9 | 1.7% | 7.19 | 2.07 | 9.12 | 7.08 | 2.03 | 8.97
Table A2.2 Demand forecast for the low scenario in calendar year format for Ireland and Northern Ireland
| Median | Calendar Year TER (TWh) | [5 empty] | TER Peak (GW) |  |  | Transmission Peak (GW)
| Year | Ireland |  | Northern Ireland |  | All-Island |  | Ireland | Northern Ireland | All-Island | Ireland | Northern Ireland | All-Island
|  | TER (TWh) | % Growth | TER (TWh) | % Growth | TER (TWh) | % Growth
| 2024 | 35.2 | 3.8% | 8.2 | 0.6% | 43.4 | 3.2% | 6.02 | 1.66 | 7.63 | 5.91 | 1.61 | 7.48
| 2025 | 36.5 | 3.8% | 8 | -2.6% | 44.5 | 2.6% | 5.98 | 1.58 | 7.61 | 5.87 | 1.54 | 7.46
| 2026 | 37.3 | 2.2% | 8 | 0.9% | 45.3 | 1.9% | 6 | 1.6 | 7.64 | 5.89 | 1.56 | 7.49
| 2027 | 38.1 | 2.1% | 8.2 | 1.9% | 46.2 | 2% | 6.05 | 1.63 | 7.72 | 5.93 | 1.59 | 7.56
| 2028 | 38.7 | 1.7% | 8.3 | 1.9% | 47 | 1.7% | 6.09 | 1.65 | 7.78 | 5.98 | 1.61 | 7.63
| 2029 | 39.4 | 1.6% | 8.5 | 1.9% | 47.8 | 1.7% | 6.14 | 1.68 | 7.85 | 6.03 | 1.64 | 7.7
| 2030 | 40 | 1.6% | 8.6 | 1.9% | 48.6 | 1.7% | 6.17 | 1.71 | 7.92 | 6.06 | 1.67 | 7.77
| 2031 | 40.6 | 1.4% | 8.9 | 2.7% | 49.4 | 1.6% | 6.21 | 1.75 | 7.97 | 6.1 | 1.71 | 7.82
| 2032 | 41.1 | 1.2% | 9.1 | 2.5% | 50.1 | 1.5% | 6.24 | 1.8 | 8.03 | 6.13 | 1.76 | 7.88
| 2033 | 41.5 | 1.2% | 9.3 | 2.5% | 50.8 | 1.4% | 6.27 | 1.85 | 8.09 | 6.16 | 1.81 | 7.94
| 2034 | 42 | 1.1% | 9.6 | 2.5% | 51.5 | 1.3% | 6.3 | 1.89 | 8.14 | 6.19 | 1.85 | 7.99
| 2035 | 42.4 | 1% | 9.8 | 2.3% | 52.2 | 1.3% | 6.32 | 1.94 | 8.2 | 6.21 | 1.9 | 8.05
Table A2.3 Demand forecast for the high scenario in calendar year format for Ireland and Northern Ireland
| Median | Calendar Year TER (TWh) | [5 empty] | TER Peak (GW) |  |  | Transmission Peak (GW)
| Year | Ireland |  | Northern Ireland |  | All-Island |  | Ireland | Northern Ireland | All-Island | Ireland | Northern Ireland | All-Island
|  | TER (TWh) | % Growth | TER (TWh) | % Growth | TER (TWh) | % Growth
| 2024 | 35.2 | 3.8% | 8.2 | 0.6% | 43.4 | 3.2% | 6.02 | 1.66 | 7.63 | 5.91 | 1.61 | 7.48
| 2025 | 37.7 | 7.1% | 8.6 | 4.8% | 46.3 | 6.7% | 6.27 | 1.7 | 7.9 | 6.15 | 1.66 | 7.75
| 2026 | 40.4 | 7.2% | 8.7 | 1.8% | 49.1 | 6.2% | 6.51 | 1.73 | 8.18 | 6.4 | 1.69 | 8.03
| 2027 | 42.9 | 6.1% | 9 | 2.9% | 51.8 | 5.5% | 6.74 | 1.78 | 8.45 | 6.62 | 1.74 | 8.3
| 2028 | 44.9 | 4.7% | 9.2 | 2.8% | 54.1 | 4.3% | 6.94 | 1.82 | 8.7 | 6.83 | 1.78 | 8.55
| 2029 | 46.8 | 4.3% | 9.5 | 3.3% | 56.3 | 4.1% | 7.14 | 1.86 | 8.92 | 7.03 | 1.82 | 8.77
| 2030 | 48.6 | 3.8% | 9.8 | 3.2% | 58.4 | 3.7% | 7.31 | 1.9 | 9.11 | 7.2 | 1.86 | 8.96
| 2031 | 50 | 3% | 10.2 | 4.1% | 60.2 | 3.2% | 7.45 | 1.97 | 9.28 | 7.34 | 1.93 | 9.13
| 2032 | 51.3 | 2.5% | 10.6 | 3.9% | 61.9 | 2.8% | 7.58 | 2.03 | 9.44 | 7.47 | 1.99 | 9.3
| 2033 | 52.3 | 2% | 11 | 3.5% | 63.3 | 2.3% | 7.67 | 2.1 | 9.58 | 7.56 | 2.06 | 9.44
| 2034 | 53.2 | 1.6% | 11.3 | 3.3% | 64.5 | 1.9% | 7.75 | 2.17 | 9.72 | 7.64 | 2.13 | 9.57
| 2035 | 53.9 | 1.4% | 11.7 | 3.3% | 65.6 | 1.7% | 7.82 | 2.23 | 9.83 | 7.71 | 2.19 | 9.68

## Appendix 3
Appendix 3: Generation Plant Information
Ireland
Table A3.1 Registered capacity of dispatchable generation and interconnectors in Ireland in 2026 (MW)
|  | ID | Fuel Type | Technology Category | 2026 | Comment
| Aghada | AT1 | Gas/DO | Gas Turbine | 90
|  | AT2 | Gas/DO | Gas Turbine | 90
|  | AT4 | Gas/DO | Gas Turbine | 90
|  | AD2 | Gas/DO | Gas Turbine | 449
| All DSU | DSU | DSU | DSU | 760
| Ardnacrusha | AA1-4 | Hydro | Hydro | 86
| Battery | Battery | Battery | Other Storage | 850
| Dublin Bay | DB1 | Gas/DO | Gas Turbine | 415 | ILC refurbishment Jun to Oct 2026
| Dublin Waste | DW1 | Waste | Steam Turbine | 61
| Edenderry | ED1 | Milled peat/ Biomass | Steam Turbine | 118
|  | ED3 | DO/Gas | Gas Turbine | 58
|  | ED5 | DO/Gas | Gas Turbine | 58
| Erne | ER1-4 | Hydro | Hydro | 65
| EWIC | EW1 |  | DC Interconnector | 500
| FlexGen | Ringsend | Gas/Multi Fuel | Gas Turbine | 64 | Newly operational as of Q4 2024
|  | Poolbeg | Gas/Multi Fuel | Gas Turbine | 64 | Newly operational as of Q4 2024
|  | Coruff | Gas/Multi Fuel | Gas Turbine | 64 | Newly operational as of Q4 2024
| Great Island CCGT | GI4 | Gas/DO | Gas Turbine | 464
| Greenlink | GLK |  | DC Interconnector | 500
| Huntstown | HNC | Gas/DO | Gas Turbine | 337 | ILC refurbishment Mar to Jul 2028
|  | HN2 | Gas/DO | Gas Turbine | 408 | ILC refurbishment Jul to Oct 2028
| Indaver Waste | IW1 | Waste | Steam Turbine | 17
| Lee | LE1-4 | Hydro | Hydro | 27
| Liffey | LI1-4 | Hydro | Hydro | 38
| Poolbeg CC | PBA | Gas/DO | Gas Turbine | 234
|  | PBB |  | Gas Turbine | 234
| Rhode | RP1 | DO | Gas Turbine | 52
|  | RP2 | DO | Gas Turbine | 52
| Sealrock | SK3 | Gas/DO | Gas Turbine | 81
|  | SK4 | Gas/DO | Gas Turbine | 81
| Tawnaghmore | TP1 | DO | Gas Turbine | 52
|  | TP3 | DO | Gas Turbine | 52
| Turlough Hill | TH1/2 | Pumped storage | Storage | 292 | ILC refurbishment Feb to Oct 2027
| Tynagh | TYC | Gas/DO | Gas Turbine | 389 | ILC refurbishment May to Jul 2027
| Whitegate | WG1 | Gas/DO | Gas Turbine | 450 | ILC refurbishment Mar to May 2027
| Total: |  |  |  | 7642
Table A3.2 Partially/non-dispatchable plant in Ireland (MW)
| At year end: | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Wind Onshore | 5740 | 6070 | 6440 | 6810 | 7130 | 7530 | 7940 | 8350 | 8770 | 9180
| Wind Offshore | 30 | 30 | 30 | 30 | 1350 | 1950 | 2520 | 3120 | 3730 | 4480
| Solar PV | 3260 | 4010 | 4770 | 5520 | 6280 | 6880 | 7480 | 8060 | 8640 | 9220
| Small Scale Hydro | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
| Biomass and Biogas | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| Biomass CHP | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
| Industrial | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
| Conventional CHP | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
| Total | 9249 | 10329 | 11459 | 12579 | 14979 | 16579 | 18159 | 19749 | 21359 | 23099
Northern Ireland
Table A3.3 Registered capacity of dispatchable generation and interconnectors in Northern Ireland in 2026 (MW)
|  | ID | Fuel Type | Technology Category | 2025 | Comment
| Ballylumford | 2026: B31; 2027: Gas/Heavy Fuel Oil; 2028: Gas Turbine; 2029: 246
|  | B32 | Gas/Heavy Fuel Oil | Gas Turbine | 246
|  | B10 | Gas/Heavy Fuel Oil | Gas Turbine | 101
|  | GT7(GT1) | Distillate Oil | Gas Turbine | 58
|  | GT8(GT2) | Distillate Oil | Gas Turbine | 58
| Kilroot | 2026: KGT1; 2027: Distillate Oil; 2028: Gas Turbine; 2029: 29
|  | KGT2 | Distillate Oil | Gas Turbine | 29
|  | KGT3 | Distillate Oil | Gas Turbine | 42
|  | KGT4 | Distillate Oil | Gas Turbine | 42
|  | KGT6 | Gas | Gas Turbine | 350
|  | KGT7 | Gas | Gas Turbine | 350
| Coolkeeragh | 2026: GT8; 2027: Distillate Oil; 2028: Gas Turbine; 2029: 53
|  | C30 | Gas/Distillate Oil | Gas Turbine | 408
| AGU | 2026: AGU; 2027: Distillate Oil; 2028: Gas Turbine; 2029: 79
| CMN | 2026: CMN; 2027: Distillate Oil; 2028: Gas Turbine; 2029: 20
| DSU | 2026: DSU; 2027: Various; 2028: DSU; 2029: 189
| Battery | 2026: Battery; 2027: Battery; 2028: Other Storage; 2029: 212
| Lisahally | 2027: Biomass; 2029: 18; 2030: Not in Capacity Market, but assumed available for capacity requirement
| Moyle | 2028: DC Interconnector; 2029: 450; 2030: Assumed to increase to 500 MW in 2028
| Total: | 2029: 2980
Table A3.4 Partially/non-dispatchable plant in Northern Ireland (MW)
| At year end: | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Onshore Wind | 1230 | 1290 | 1370 | 1520 | 1670 | 1820 | 1970 | 2120 | 2270 | 2420
| Offshore Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500
| Small Scale Wind | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
| Solar PV | 270 | 300 | 350 | 410 | 480 | 550 | 620 | 690 | 760 | 830
| Small Scale Biogas | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| Landfill Gas | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
| Small Scale Biomass | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Renewable CHP | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Other CHP | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Small Scale Hydro | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Waste-to-Energy | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
| Total | 1756 | 1846 | 1976 | 2186 | 2406 | 2626 | 2846 | 3066 | 3286 | 4006
Table A3.5 All renewable energy sources in Northern Ireland (MW)
| At year end: | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| All Wind | 1410 | 1470 | 1550 | 1700 | 1850 | 2000 | 2150 | 2300 | 2450 | 3100
| Solar PV | 270 | 300 | 350 | 410 | 480 | 550 | 620 | 690 | 760 | 830
| All Biomass/Biogas/LFGas/WTE | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
| Renewable CHP | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Hydro | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Total RES | 1735 | 1825 | 1955 | 2165 | 2385 | 2605 | 2825 | 3045 | 3265 | 3985

## System Inputs - IE
Ireland Modelling Inputs
Ireland demand and operational requirements
|  |  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| AIRAA 2026-2035 Median Transmission Peak Demand (MW) |  | 6173 | 6307 | 6435 | 6562 | 6682 | 6788 | 6880 | 6964 | 7027 | 7084
| Reserve Requirement (MW) |  | 375 | 375 | 525 | 525 | 525 | 525 | 525 | 525 | 525 | 525
| Transmission Outage Planning (MW) |  | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350
Ireland generation portfolio unit capacities
The modelling of the system’s ability to meet the fluctuating demand is a complex function of combined probabilities of forced outage rates, optimisation of scheduled outage, annual run hour limitations and storage capacity and duration. As such, a simple comparison of the demand and total capacities here is not indicative of the adequacy position. The rated capacities and availabilities below are the inputs provided into that complex function.
Rated Capacity (MW)
| Plant Name | ID | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Aghada | AT1 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | AT2 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | AT4 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | AD2 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449
| Ardnacrusha | AA1 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  | AA2 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  | AA3 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  | AA4 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| Dublin Bay | DB1 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
| Dublin Waste | DW1 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
| Edenderry | ED1 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118
|  | ED3 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
|  | ED5 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
| Erne | ER1 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | ER2 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | ER3 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  | ER4 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
| Flexgen | Ringsend | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
|  | Poolbeg | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
|  | Coruff | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
| Great Island CCGT | GI4 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464
| Huntstown | HNC | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336
|  | HN2 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408
| Indaver Waste | IW1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
| Lee | LE1 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
|  | LE2 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  | LE3 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
| Liffey | LI1 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
|  | LI2 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
|  | LI3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  | LI4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Moneypoint | MP1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | MP2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | MP3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Poolbeg CC | PBA | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234
|  | PBB | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234
| Rhode | RP1 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
|  | RP2 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
| Sealrock | SK3 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
|  | SK4 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
| Tawnaghmore | TP1 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
|  | TP3 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
| Tynagh | TYC | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389
| Whitegate | WG1 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450
New In-Market conventional generation portfolio
Cumulative Rated Capacity (MW)
|  | Plant Name | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
|  | Gas Turbine Auction Results | 900 | 2060 | 2110 | 2450 | 2450 | 2450 | 2450 | 2450 | 2450 | 2450
|  | Gas Turbine Auction Risk Adjusted Delivery | 610 | 910 | 1500 | 1900 | 1900 | 1900 | 1900 | 1900 | 1900 | 1900
Energy storage portfolio
|  | Type | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
|  | Rated Capacity (MW) | 1140 | 1280 | 1370 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800 | 1800
|  | Energy Storage (MWh) | 2770 | 3280 | 3400 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760 | 4760
Inclusive of battery and pumped hydroelectric storage
Demand Side Unit portfolio
|  | Type | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
|  | Rated Capacity (MW) | 569 | 521 | 567 | 749 | 749 | 749 | 749 | 749 | 749 | 749
Interconnection portfolio
Net Transfer Capacity (MW) [2]
|  | Unit | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Import | EWIC | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
|  | Greenlink | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
|  | Celtic [3] | 0 | 0 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700
|  | North - South [4] | 300 | 300 | 300 | 300 | 300 | 300 | 1200 | 1200 | 1200 | 1200
| Export | EWIC | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
|  | Greenlink | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
|  | Celtic [3] | 0 | 0 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700
|  | North - South [4] | 300 | 300 | 300 | 300 | 300 | 300 | 1250 | 1250 | 1250 | 1250
[2] Rated transfer capacity to be used in economic dispatch model.
[3] Interconnector has not yet been commissioned, assumed available Q2 2028.
[4] New North South included for the All-Island assessment only from October 2031.
Ireland generation portfolio wind and solar capacities
Rated Capacity (MW)
|  |  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
|  | Offshore Wind | 25 | 25 | 25 | 25 | 1354 | 1952 | 2516 | 3118 | 3727 | 4481
|  | Onshore Wind | 5744 | 6068 | 6441 | 6811 | 7130 | 7533 | 7939 | 8350 | 8770 | 9189
|  | Solar | 3261 | 4014 | 4768 | 5521 | 6279 | 6883 | 7476 | 8061 | 8639 | 9222
|  | Hydro | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216 | 216
Other RES / other non-RES portfolio
Rated Capacity (MW)
|  | Type | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Industrial | INDU | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
| Small Scale Hydro | SSH | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
| Conventional CHP | CHP | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129
| Landfill Gas | LFG | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| CHP_Bio | CHP Bio | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
All-island availability statistics
| Technology Category | Mean Forced Outage Probability (%) | Rated Capacity (MW) 2026: Mean Scheduled Outage Rate (%); Rated Capacity (MW) 2027: Mean Scheduled Outage Duration (hours); Rated Capacity (MW) 2028: Annual Availability (%)
| DSU | * | Rated Capacity (MW) 2026: *; Rated Capacity (MW) 2027: *; Rated Capacity (MW) 2028: 26.2
| DSU Run Hour Limited | * | Rated Capacity (MW) 2026: *; Rated Capacity (MW) 2027: *; Rated Capacity (MW) 2028: 23.4
| Gas Turbine | 11.1 | Rated Capacity (MW) 2026: 4.8; Rated Capacity (MW) 2027: 420; Rated Capacity (MW) 2028: 84.1
| Hydro | 13.4 | Rated Capacity (MW) 2026: 5.9; Rated Capacity (MW) 2027: 520; Rated Capacity (MW) 2028: 80.7
| Steam Turbine | 15.9 | Rated Capacity (MW) 2026: 7.6; Rated Capacity (MW) 2027: 660; Rated Capacity (MW) 2028: 76.5
| Interconnector | 4.5 | Rated Capacity (MW) 2026: 3.8; Rated Capacity (MW) 2027: 340; Rated Capacity (MW) 2028: 91.7
| Pumped Hydro Storage | 2.7 | Rated Capacity (MW) 2026: 5.2; Rated Capacity (MW) 2027: 450; Rated Capacity (MW) 2028: 92.1
| Other Storage*** | 5.1 | Rated Capacity (MW) 2026: **; Rated Capacity (MW) 2027: **; Rated Capacity (MW) 2028: 94.9
| System Wide | 21.1 | Rated Capacity (MW) 2026: 6.1; Rated Capacity (MW) 2027: 540; Rated Capacity (MW) 2028: 72.7
* In line with the monthly availability reporting, availability of DSUs considers a capacity-weighted availability instead of forced and scheduled outage statistics.
** Scheduled outages for battery storage units were observed to be close to 0% and therefore have not been included as part of this assessment.
*** Other Storage statistics are based on one year of availability data, which will be expanded on over the coming years as more data becomes available.

## System Inputs - NI
Northern Ireland Modelling Inputs
Northern Ireland demand and operational requirements
|  |  | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| AIRAA 2026 - 2035 Median Transmission Peak Demand (MW) |  | 1610.7757 | 1648.824 | 1686.2072 | 1717.3716 | 1752.1807 | 1810.9268 | 1857.3203 | 1921.6025 | 1973.344 | 2027.4315
| Reserve Requirement (MW) |  | 125 | 125 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175
Northern Ireland generation portfolio unit capacities
The modelling of the system’s ability to meet the fluctuating demand is a complex function of combined probabilities of forced outage rates, optimisation of scheduled outage, annual run hour limitations and storage capacity and duration. As such, a simple comparison of the demand and total capacities here is not indicative of the adequacy position. The rated capacities and availabilities below are the inputs provided into that complex function.
Rated Capacity (MW)
| Plant Name | ID | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| AGU | AGU | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
| CMN | CMN | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
| Coolkeeragh | GT8 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53
|  | C30 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408
| Ballylumford | B31 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246
|  | B32 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246
|  | B10 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101
|  | GT7(GT1) | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
|  | GT8(GT2) | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
| Kilroot | KGT1 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
|  | KGT2 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
|  | KGT3 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
|  | KGT4 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
|  | KGT6 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350
|  | KGT7 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350
| Lisahally | Lisahally | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
Energy storage portfolio
|  | Type | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
|  | Rated Capacity (MW) | 210 | 210 | 220 | 240 | 240 | 240 | 240 | 240 | 240 | 240
|  | Energy Storage (MWh) | 160 | 160 | 190 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Demand Side Unit portfolio
|  | Type | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
|  | Rated Capacity (MW) | 137 | 80 | 117 | 130 | 130 | 130 | 130 | 130 | 130 | 130
Interconnection portfolio
Net Transfer Capacity (MW) [1]
|  | Unit | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| Import | Moyle | 450 | 450 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
|  | North - South [2] | 300 | 300 | 300 | 300 | 300 | 300 | 1250 | 1250 | 1250 | 1250
| Export | Moyle | 400 | 400 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
|  | North - South [2] | 300 | 300 | 300 | 300 | 300 | 300 | 1200 | 1200 | 1200 | 1200
[1] Rated transfer capacity to be used in economic dispatch model.
[2] New North South included for the All-Island assessment only from October 2031.
Wind and solar portfolio
Rated Capacity (MW)
|  | Source | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
|  | Offshore Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500
|  | Onshore Wind | 1410 | 1470 | 1550 | 1700 | 1850 | 2000 | 2150 | 2300 | 2450 | 2600
|  | Solar | 270 | 300 | 350 | 410 | 480 | 550 | 620 | 690 | 760 | 830
Other RES / other non-RES portfolio
Rated Capacity (MW)
|  | Type | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035
| CHP | NI_CHP | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Biogas | NI_BIOGAS | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| Biomass | NI_BIOMASS | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Renewable CHP | NI_CHP_RES | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Hydro | NI_SSH | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Landfill Gas | NI_LFG | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
| Diesel | NI_DIESEL | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
All-island availability statistics
| Technology Category | Mean Forced Outage Probability (%) | 2026: Mean Scheduled Outage Rate (%); 2027: Mean Scheduled Outage Duration (hours); 2028: Annual Availability (%)
| DSU | * | 2026: *; 2027: *; 2028: 26.2
| DSU Run Hour Limited | * | 2026: *; 2027: *; 2028: 23.4
| Gas Turbine | 11.1 | 2026: 4.8; 2027: 420; 2028: 84.1
| Hydro | 13.4 | 2026: 5.9; 2027: 520; 2028: 80.7
| Steam Turbine | 15.9 | 2026: 7.6; 2027: 660; 2028: 76.5
| Interconnector | 4.5 | 2026: 3.8; 2027: 340; 2028: 91.7
| Pumped Hydro Storage | 2.7 | 2026: 5.2; 2027: 450; 2028: 92.1
| Other Storage*** | 5.1 | 2026: **; 2027: **; 2028: 94.9
| System Wide | 21.1 | 2026: 6.1; 2027: 540; 2028: 72.7
* In line with the monthly availability reporting, availability of DSUs considers a capacity-weighted availability instead of forced and scheduled outage statistics.
** Scheduled outages for battery storage units were observed to be close to 0% and therefore have not been included as part of this assessment.
*** Other Storage statistics are based on one year of availability data, which will be expanded on over the coming years as more data becomes available.