## Front Page
All Island Resource Adequacy Assessment 2025-2034 Data Workbook
Purpose: To publically share the data used throughout the All-Island Resource Adequacy Assessment 2025-2034. For any questions on this data, please contact info@EirGrid.com or info@SONI.ltd.uk, referencing the All-Island Resource Adequacy Assessment 2025-2034 in the subject line.
Disclaimer: EirGrid Plc and SONI Ltd have followed accepted industry practice in the collection and analysis of data available. While all reasonable care has been taken in the preparation of this data, EirGrid and SONI are not responsible for any loss that may be attributed to the use of this information. Prior to taking business decisions, interested parties are advised to seek separate and independent opinion in relation to the matters covered by this report and should not rely solely upon data and information contained herein. Information in this document does not amount to a recommendation in respect of any possible investment. This document does not purport to contain all the information that a prospective investor or participant in the Single Electricity Market (SEM) may need.
Version History:
| Version | Description | Date
| 1 | Initial Publication | March 2025
Contents (In order shown in report):
| Location in Report | Description | Link
| Table 4.1 | Average annual growths for macroeconomic parameters, values used for median demand as advised by the ESRI. | Demand IE
| Table 4.2 | Forecasted data centre and new technology load demand by 2034. 2023 demand 867 MVA. | Demand IE
| Figure 4.1 | Ireland demand expected from assumed build out of data centres and new technology loads. | Demand IE
| Table 4.3 | Climate Action Plan 2024 targets for electric vehicles and heat pumps out to 2030. | Demand IE
| Figure 4.2 | Electric vehicle electrical energy demand - median scenario | Demand IE
| Figure 4.2 | Heat pump electrical energy demand - median scenario | Demand IE
| Figure 4.3 | Historic recorded and temperature corrected peak demand | Demand IE
| Figure 4.4 | Impact of demand flexibility on 2030 peak day (median scenario) | Demand IE
| Figure 4.5 | Impact of demand flexibility in median scenario across the study period | Demand IE
| Figure 4.6 | Total Electricity Requirement for Ireland | Demand IE
| Table 4.4 | Low, median and high Total Electricity Requirement key assumption differences | Demand IE
| Figure 4.7 | Ireland median demand Total Electricity Requirement sectoral breakdown | Demand IE
| Figure 4.8 | Sectoral contribution to Ireland's TER in 2025 & 2034 | Demand IE
| Figure 4.9 | Sectoral contribution to Ireland's peak demand in 2025 & 2034 | Demand IE
| Figure 4.10 | Transmission peak forecast for Ireland | Demand IE
| Table 4.5 | Low, median, high peak demand key assumption differences | Demand IE
| Figure 4.11 | Impact of climate variability in Ireland on peak demand | Demand IE
| Figure 4.12 | Forecast hourly demand shape in Ireland | Demand IE
| Figure 4.13 | Electric vehicle charging profiles | Demand IE
| Table 4.6 | Number of electric vehicles and heat pump installations included in the low, median, and high demand forecast | Demand NI
| Figure 4.14 | Northern Ireland TER forecast | Demand NI
| Figure 4.15 | Northern Ireland TER forecast components | Demand NI
| Table 4.7 | Low, median and high Total Electricity Requirement key assumption differences | Demand NI
| Figure 4.16 | ACS transmission peak forecasts for Northern Ireland | Demand NI
| Table 4.8 | Low, median and high peak demand key assumption differences | Demand NI
| Figure 4.17 | Impact of demand flexibility on 2030 peak day (median scenario) | Demand NI
| Figure 4.18 | Impact of demand flexibility in median scenario across the study period | Demand NI
| Figure 4.19 | Combined TER forecast for all-island system | Demand AI
| Figure 4.20 | TER peak for the combined all-island forecast | Demand AI
| Figure 5.1 | Age breakdown of dispatchable plant for the All-Island system operational in 2025 | Generation - All Island
| Figure 5.2 | Conventional generation portfolio assumed in Ireland | Generation - Conventional IE
| Table 5.1 | Ireland assumptions for new conventional plant capacities in adequacy studies (rated MW). This risk adjusted view is based on plant delivering early, delivering late, or not delivering. For reference, the capacity successful in capacity auctions that has not received a termination notice is also presented. Note all values are rounded to the nearest 10 MW and capacity is presented as capacity commissioning during the calendar year. | Generation - Conventional IE
| Table 5.2 | Assumptions for conventional plant changes in Ireland | Generation - Conventional IE
| Figure 5.3 | Conventional generation portfolio assumed in Northern Ireland | Generation - Conventional NI
| Table 5.3 | Capacity (MW) assumed to be subject to run hour limits in Ireland | Generation - Conventional IE
| Table 5.4 | Capacity (MW) assumed to be subject to run hour limits in Northern Ireland | Generation - Conventional NI
| Table 5.5 | North South Tie Line net transfer capacity | Generation - All Island
| Table 5.6 | HVDC net transfer capacity (MW) assumptions | Generation - All Island
| Table 5.7 | Further interconnection projects | Generation - All Island
| Table 5.8 | Climate Action Plan renewable targets in Ireland | Generation - Renewable IE
| Figure 5.4 | Assumed growth of variable generation capacity in Ireland | Generation - Renewable IE
| Figure 5.5 | Assumed growth of variable generation capacity in Northern Ireland | Generation - Renewable NI
| Table 5.9 | Ireland energy storage capacity (MW) | Generation - Non-Conventional
| Table 5.10 | Ireland energy storage (MWh) | Generation - Non-Conventional
| Table 5.11 | Northern Ireland energy storage capacity (MW) | Generation - Non-Conventional
| Table 5.12 | Northern Ireland energy storage (MWh) | Generation - Non-Conventional
| Table 5.13 | Ireland DSU capacity (MW) | Generation - Non-Conventional
| Table 5.14 | Ireland DSU run hour restriction (hours) | Generation - Non-Conventional
| Table 5.15 | Northern Ireland DSU capacity (MW) | Generation - Non-Conventional
| Table 5.16 | Northern Ireland DSU run hour restriction (hours) | Generation - Non-Conventional
| Table 5.17 | Northern Ireland AGU capacity (MW) | Generation - Non-Conventional
| Table 5.18 | Summary of technology class availability statistics | Generation - Availability
| Figure 5.6 | All-island average annual generation capacity availability for the past 10 years (excluding DSU) | Generation - Availability
| Figure 5.7 | Average annual conventional generation capacity forced and scheduled outage rates in Ireland for the past 10 years | Generation - Availability
| Figure 5.8 | Average annual conventional generation capacity forced and scheduled outage rates in Northern Ireland for the past 10 years | Generation - Availability
| Figure 5.9 | Ireland and Northern Ireland conventional generation capacity availability across the last 5 years | Generation - Availability
| Figure 5.10 | All-Island demand side unit monthly availability for 2022 and 2023 calendar years | Generation - Availability
| Table 6.1 | LOLE standards | Adequacy
| Figure 6.1 | Adequacy modelling process overview | Adequacy
| Figure 6.2 | Base and Secure surplus/deficit results for Ireland | Adequacy
| Figure 6.3 | Distribution of LOLE Base results for the Ireland median demand scenario where each low/mid/high band represents 1/3rd of the 35 climate year results (includes reserves) | Adequacy
| Table 6.2 | LOLE and EENS Base results for Ireland (includes reserves) | Adequacy
| Table 6.3 | LOLE and EENS Base Demand Only results for Ireland (excludes reserves) | Adequacy
| Table 6.4 | Average LOLE of the 3 climate years used in the surplus/deficit calculation for Ireland (includes reserves) | Adequacy
| Figure 6.4 | MW Base results for Ireland in terms of surplus (+) and deficit (-) of perfect plant | Adequacy
| Table 6.5 | MW Base results for Ireland in terms of surplus (+) and deficit (-) of perfect plant | Adequacy
| Figure 6.5 | Sensitivity analysis for Ireland in terms of deficit (-) of perfect plant impact | Adequacy
| Figure 6.6 | Distribution of LOLE Secure results for the Ireland median demand scenario where each low/mid/high band represents 1/3rd of the 35 climate year results (includes reserves) | Adequacy
| Table 6.6 | LOLE and EENS Secure results for Ireland (includes reserves) | Adequacy
| Figure 6.7 | Secure surplus/deficit results for Ireland in terms of surplus (+) and deficit (-) of perfect plant | Adequacy
| Table 6.7 | Secure surplus/deficit results for Ireland in terms of surplus (+) and deficit (-) of perfect plant | Adequacy
| Figure 6.8 | Sensitivity analysis for Ireland | Adequacy
| Table 6.8 | Low renewable deployment scenario (MW) | Adequacy
| Table 6.9 | SOEF v1.1 low emissions trajectory (MW) | Adequacy
| Figure 6.9 | Ireland adequacy position with mitigating measures | Adequacy
| Figure 6.10 | Base and Secure surplus/deficit results for Northern Ireland | Adequacy
| Figure 6.11 | Distribution of LOLE Base results for the Northern Ireland median demand scenario where each low/mid/high band represents 1/3rd of the 35 climate year results (includes reserves) | Adequacy
| Table 6.10 | LOLE and EENS Base results for Northern Ireland (includes reserves) | Adequacy
| Table 6.11 | LOLE and EENS Base Demand Only results for Northern Ireland (excludes reserves) | Adequacy
| Table 6.12 | Average LOLE of the 3 climate years used in the surplus/deficit calculation for Northern Ireland (includes reserves) | Adequacy
| Figure 6.12 | MW Base results for Northern Ireland in terms of surplus (+) and deficit (-) of perfect plant | Adequacy
| Table 6.13 | MW Base results for Northern Ireland in terms of surplus (+) and deficit (-) of perfect plant | Adequacy
| Figure 6.13 | Sensitivity analysis for Northern Ireland in terms of deficit (-) of perfect plant impact | Adequacy
| Figure 6.14 | Distribution of LOLE Secure results for the Northern Ireland median demand scenario where each low/mid/high band represents 1/3rd of the 35 climate year results (includes reserves) | Adequacy
| Table 6.14 | LOLE and EENS Secure results for Northern Ireland (includes reserves) | Adequacy
| Figure 6.15 | MW Secure results for Northern Ireland in terms of surplus (+) and deficit (-) of perfect plant | Adequacy
| Table 6.15 | MW Secure results for Northern Ireland in terms of surplus (+) and deficit (-) of perfect plant | Adequacy
| Figure 6.16 | Sensitivity analysis for Northern Ireland | Adequacy
| Table 6.16 | Northern Ireland low renewable trajectory (MW) | Adequacy
| Table 6.17 | Northern Ireland high renewable trajectory (MW) | Adequacy
| Table 6.18 | Base results for the all-island system | Adequacy
| Figure 6.17 | Base scenario adequacy analysis for the all-island system in terms of surplus (+) and deficit (-) of perfect plant | Adequacy
| Table 6.19 | Secure results for the all-island system | Adequacy
| Figure 6.18 | Secure scenario adequacy analysis for the all-island system in terms of surplus (+) and deficit (-) of perfect plant | Adequacy
| Table A1.1 | Demand forecast for the median scenario in calendar year format for Ireland and Northern Ireland | Appendix 1
| Table A1.2 | Demand forecast for the low scenario in calendar year format for Ireland and Northern Ireland | Appendix 1
| Table A1.3 | Demand forecast for the high scenario in calendar year format for Ireland and Northern Ireland | Appendix 1
| Table A2.1 | Capacity auction results | Appendix 2
| Table A2.2 | Terminated awarded new capacity | Appendix 2
| Table A3.1 | Registered capacity of dispatchable generation and interconnectors in Ireland in 2025 (MW) | Appendix 3
| Table A3.2 | All renewable energy sources in Ireland (MW) | Appendix 3
| Table A3.3 | Registered capacity of dispatchable generation and interconnectors in Northern Ireland in 2025 (MW) | Appendix 3
| Table A3.4 | Partially/Non-Dispatchable plant in Northern Ireland (MW) | Appendix 3
| Table A3.5 | All renewable energy sources in Northern Ireland (MW) | Appendix 3
| Figure A4.1 | Results of adequacy alignment for Ireland given in MW in terms of surplus (+) and deficit (-) of perfect plant | Appendix 4
| Table A4.1 | Results of adequacy alignment for Ireland given in MW in terms of surplus (+) and deficit (-) of perfect plant | Appendix 4
| Figure A4.2 | Results of adequacy alignment for Northern Ireland given in MW in terms of surplus (+) and deficit (-) of perfect plant | Appendix 4
| Figure A4.2 | Results of adequacy alignment for Northern Ireland given in MW in terms of surplus (+) and deficit (-) of perfect plant | Appendix 4

## Demand - IE
Demand Forecast for Ireland
4.2.2 Economic forecast
Table 4.1 Average annual growths for macroeconomic parameters, values used for median demand as advised by the ESRI.
|  | 2023-2024 |  |  | 2025-2034
|  | Low (75% ESRI) | Median (ESRI) | High (110% ESRI) | Low (75% ESRI) | Median (ESRI) | High (110% ESRI)
| Real GNI* | 0.98% | 1.3% | 1.43% | 2.25% | 3% | 3.3%
| Personal Consumption | 2.2% | 2.9% | 3.2% | 1.88% | 2.5% | 2.75%
4.2.3 Data centres and new technology loads
Table 4.2 Forecasted data centre and new technology load demand by 2034. 2023 demand 867 MVA.
| Forecast Scenario | Growth from 2023-2034 (MVA) | 2034 Demand (MVA)
| Low | 422 | 1289
| Median | 813 | 1680
| High | 1200 | 2067
Figure 4.1 Ireland demand expected from assumed build out of data centres and new technology loads.
| Year | Historical (MVA) | Low Scenario (MVA) | Median Scenario (MVA) | High Scenario (MVA) | Contract Ramp (MVA)
| 2016 | 196.5
| 2017 | 262
| 2018 | 357.24
| 2019 | 431.5
| 2020 | 519.7759
| 2021 | 600.1
| 2022 | 733.5
| 2023 | 867
| 2024 |  | 902.2 | 1009 | 1133.5 | 1749.5
| 2025 |  | 967.95 | 1144.6 | 1376.25 | 1926.2
| 2026 |  | 1030.3 | 1280.45 | 1587.45 | 2123.7
| 2027 |  | 1067.05 | 1347.65 | 1699.65 | 2197.2
| 2028 |  | 1103.05 | 1411.85 | 1804.05 | 2230.7
| 2029 |  | 1137.8 | 1469.35 | 1893.3 | 2266.6
| 2030 |  | 1171.55 | 1525.3 | 1964.5 | 2272.6
| 2031 |  | 1203.8 | 1575.15 | 2000.5 | 2272.6
| 2032 |  | 1234.55 | 1615.65 | 2024.18 | 2272.6
| 2033 |  | 1262.05 | 1654.15 | 2045.68 | 2272.6
| 2034 |  | 1288.8 | 1679.65 | 2067.18 | 2272.6
4.2.4 Electrification of heat and transport
Table 4.3 Climate Action Plan 2024 targets for electric vehicles and heat pumps out to 2030.
|  | Electric Vehicles |  |  | Heat Pumps
|  | Passenger | Commercial |  | Residential - New Builds | Residential - Retrofits | Commercial
| 2025 | 175000 | 10300 |  | 170000 | 45000 | 25000
| 2030 | 845000 | 82250 |  | 280000 | 400000 | 50000
Figure 4.2 Electric vehicle electrical energy demand - median scenario
| Year | BEVs (TWh) | PHEVs (TWh) | Commercial (TWh) | Total (TWh)
| 2022 | 0.11451 | 0.038643 | 0.0212 | 0.17435
| 2023 | 0.18803 | 0.057478 | 0.028799 | 0.2743
| 2024 | 0.24347 | 0.077417 | 0.036475 | 0.35736
| 2025 | 0.29682 | 0.097603 | 0.072049 | 0.46647
| 2026 | 0.41142 | 0.1356 | 0.12345 | 0.67047
| 2027 | 0.56203 | 0.17855 | 0.18977 | 0.93035
| 2028 | 0.77202 | 0.22988 | 0.26928 | 1.2712
| 2029 | 0.98971 | 0.27435 | 0.3603 | 1.6244
| 2030 | 1.1903 | 0.3071 | 0.46118 | 1.9586
| 2031 | 1.44 | 0.34577 | 0.58691 | 2.3727
| 2032 | 1.6965 | 0.3783 | 0.72746 | 2.8022
| 2033 | 1.9563 | 0.40445 | 0.88264 | 3.2434
| 2034 | 2.2162 | 0.4242 | 1.0522 | 3.6927
Figure 4.2 Heat pump electrical energy demand - median scenario
| Year | New Builds - Residential (TWh) | Retrofits - Residential (TWh) | Commercial (TWh) | Total (TWh)
| 2022 | 0.21698 | 0.059225 | 0.35661 | 0.63281
| 2023 | 0.29702 | 0.080252 | 0.37943 | 0.7567
| 2024 | 0.40519 | 0.10837 | 0.45942 | 0.97298
| 2025 | 0.54 | 0.14294 | 0.58776 | 1.2707
| 2026 | 0.6316 | 0.25187 | 0.73977 | 1.6232
| 2027 | 0.71156 | 0.40178 | 0.89627 | 2.0096
| 2028 | 0.77227 | 0.59861 | 0.99114 | 2.362
| 2029 | 0.80668 | 0.84787 | 1.0413 | 2.6958
| 2030 | 0.80826 | 1.1547 | 1.0649 | 3.0278
| 2031 | 0.94767 | 1.3538 | 1.1075 | 3.4089
| 2032 | 1.0871 | 1.553 | 1.1501 | 3.7901
| 2033 | 1.2265 | 1.7521 | 1.1926 | 4.1713
| 2034 | 1.3659 | 1.9513 | 1.2352 | 4.5524
Table 4.4 Low, median and high Total Electricity Requirement key assumption differences
|  | Low | Median | High
| Number of Electric Vehicles | 75% Climate Action Plan Targets | 100% Climate Action Plan Targets | 110% Climate Action Plan Targets
| Number of Domestic and Commercial Heat Pumps | 75% Climate Action Plan Targets | 100% Climate Action Plan Targets | 110% Climate Action Plan Targets
| Data Centre and New Technology Loads | Low Ramp | Median Ramp | High Ramp
| Economic Growth Projection | 75% ESRI Economic Projection | 100% ESRI Economic Projection | 110% ESRI Economic Projection
4.2.5 Temperature correction
Figure 4.3 Historic recorded and temperature corrected peak demand
| Year | Network Exported Peak (MW) | Historic Temperature-Corrected Peak (MW)
| 2007/08 | 4914 | 5110
| 2008/09 | 4891 | 4900
| 2009/10 | 4992 | 4870
| 2010/11 | 5090 | 4900
| 2011/12 | 4640 | 4820
| 2012/13 | 4589 | 4730
| 2013/14 | 4523 | 4800
| 2014/15 | 4695 | 4890
| 2015/16 | 4668 | 4970
| 2016/17 | 4751.87 | 4970
| 2017/18 | 4939.61 | 5050
| 2018/19 | 4910 | 5180
| 2019/20 | 5007 | 5150
| 2020/21 | 5335 | 5370
| 2021/22 | 5346 | 5530
| 2022/23 | 5508.36 | 5470
| 2023/24 | 5567 | 5653.3638
4.2.6 Peak demand forecasting – demand flexibility
Figure 4.4 Impact of demand flexibility on 2030 peak day (median scenario)
| Hr | No Flexibility Services or Incentives (MW) | 8.8% Residential Demand Reduction from Flexibility Services & Incentives (MW) | 8% Residential Demand Reduction and Flexible EV Charging Profile (MW)
| 0 | 5309.295 | 5307.8047 | 5623.5609
| 1 | 5113.3469 | 5113.4891 | 5417.5248
| 2 | 4985.6512 | 4986.8597 | 5286.0114
| 3 | 4906.6167 | 4908.4697 | 5204.8405
| 4 | 4910.8876 | 4912.81 | 5062.4897
| 5 | 4981.1916 | 4982.6376 | 5001.7059
| 6 | 5293.748 | 5292.7676 | 5213.2754
| 7 | 5849.1455 | 5843.7834 | 5670.863
| 8 | 6143.4698 | 6135.8043 | 5975.7506
| 9 | 6296.2909 | 6287.3438 | 6133.6027
| 10 | 6369.7344 | 6359.9651 | 6300.6286
| 11 | 6376.4783 | 6366.4551 | 6303.5506
| 12 | 6374.8683 | 6364.6492 | 6301.6557
| 13 | 6319.8865 | 6309.8985 | 6238.4799
| 14 | 6251.7449 | 6242.1569 | 6169.8925
| 15 | 6303.9985 | 6294.0026 | 6222.8142
| 16 | 6557.2815 | 6545.4545 | 6391.2372
| 17 | 6971.138 | 6764.1122 | 6581.569
| 18 | 6920.304 | 6713.8134 | 6541.9147
| 19 | 6734.8591 | 6529.976 | 6380.095
| 20 | 6518.3039 | 6507.3246 | 6521.5063
| 21 | 6243.8882 | 6235.1229 | 6258.0237
| 22 | 5875.8172 | 5869.9536 | 5896.7085
| 23 | 5644.6321 | 5640.601 | 5670.019
Figure 4.5 Impact of demand flexibility in median scenario across the study period
| Year | No Flexibility Services or Incentives (MW) | 8.8% Residential Demand Reduction from Flexibility Services & Incentives (MW) | 8.8% Residential Demand Reduction and Flexible EV Charging Profile (MW)
| 2023 | 5782.9239 | 5765.225 | 5756.8135
| 2024 | 6003.2172 | 5964.563 | 5945.0103
| 2025 | 6226.6787 | 6166.6153 | 6129.8746
| 2026 | 6470.7898 | 6389.2248 | 6320.2915
| 2027 | 6677.6444 | 6574.3056 | 6456.2792
| 2028 | 6881.2451 | 6756.7265 | 6564.8901
| 2029 | 7066.2698 | 6919.8125 | 6635.6109
| 2030 | 7236.3122 | 7068.1856 | 6716.2344
| 2031 | 7438.967 | 7269.9291 | 6821.1218
| 2032 | 7614.5242 | 7445.0509 | 6915.003
| 2033 | 7807.2573 | 7636.438 | 7022.9375
| 2034 | 7988.9074 | 7817.2276 | 7118.7475
4.2.8 Total Electricity Requirement (TER)
Figure 4.6 Total Electricity Requirement for Ireland
|  | Historical (TWh) | 2024 All Island Resource Adequacy Assessment (TWh) |  |  | GCS23 (TWh)
| Year |  | Low | Median | High | GCS23 Low | GCS23 Median | GCS23 High
| 2017 | 29.3759
| 2018 | 29.8143
| 2019 | 30.6167
| 2020 | 30.8684
| 2021 | 32.1888
| 2022 | 33.0694 |  |  |  | 33.2979 | 33.344 | 33.3625
| 2023 | 34.0447 | 34.0447 | 34.0447 | 34.0447 | 34.2602 | 34.8823 | 35.3028
| 2024 |  | 35.061 | 35.846 | 36.3535 | 34.95 | 36.48 | 37.92
| 2025 |  | 35.7293 | 37.7266 | 39.1782 | 35.58 | 38 | 40.39
| 2026 |  | 36.5907 | 39.4992 | 41.8684 | 36.24 | 39.58 | 42.59
| 2027 |  | 37.3883 | 41.1078 | 44.0519 | 37.08 | 41.03 | 44.89
| 2028 |  | 37.9983 | 42.3642 | 45.6859 | 37.83 | 42.27 | 46.87
| 2029 |  | 38.5965 | 43.5465 | 47.2058 | 38.49 | 43.5 | 48.41
| 2030 |  | 39.1709 | 44.6697 | 48.5474 | 39.17 | 44.73 | 49.79
| 2031 |  | 39.8869 | 45.9511 | 49.8327 | 40.02 | 46.17 | 51.31
| 2032 |  | 40.606 | 47.1819 | 50.9169 | 40.9 | 47.62 | 52.86
| 2033 |  | 41.3154 | 48.3764 | 51.949
| 2034 |  | 42.0151 | 49.5152 | 52.9815
Table 4.4 Low, median and high Total Electricity Requirement key assumption differences
|  | Low | Median | High
| Number of Electric Vehicles | 75% Climate Action Plan Targets | 100% Climate Action Plan Targets | 110% Climate Action Plan Targets
| Number of Domestic and Commercial Heat Pumps | 75% Climate Action Plan Targets | 100% Climate Action Plan Targets | 110% Climate Action Plan Targets
| Data Centre and New Technology Loads | Low Ramp | Median Ramp | High Ramp
| Economic Growth Projection | 75% ESRI Economic Projection | 100% ESRI Economic Projection | 110% ESRI Economic Projection
Figure 4.7 Ireland median demand Total Electricity Requirement sectoral breakdown
|  | Residential (TWh) | Commercial (TWh) | Industrial (TWh) | Electric Vehicles (TWh) | Heat Pumps (TWh) | Data Centres & New Tech Loads (TWh) | TER incorporating losses (TWh)
| 2020 | 9.0166 | 8.4438 | 6.3698 | 0.033965 | 0.51604 | 4.1552 | 30.8684
| 2021 | 9.0575 | 8.7904 | 6.6314 | 0.072671 | 0.61472 | 4.8916 | 32.1888
| 2022 | 8.4565 | 9.0674 | 6.8403 | 0.17435 | 0.63281 | 5.8252 | 33.0694
| 2023 | 8.2636 | 8.9182 | 6.7535 | 0.2743 | 0.7567 | 6.991 | 34.0447
| 2024 | 8.3685 | 8.8492 | 6.8019 | 0.35736 | 0.97298 | 8.1944 | 35.846
| 2025 | 8.4448 | 8.7809 | 6.9468 | 0.46647 | 1.2707 | 9.4069 | 37.7266
| 2026 | 8.5043 | 8.6955 | 6.9044 | 0.67047 | 1.6232 | 10.5926 | 39.4992
| 2027 | 8.5636 | 8.6109 | 6.9196 | 0.93035 | 2.0096 | 11.4795 | 41.1078
| 2028 | 8.5872 | 8.4929 | 6.9441 | 1.2712 | 2.362 | 12.0535 | 42.3642
| 2029 | 8.6097 | 8.3764 | 6.9482 | 1.6244 | 2.6958 | 12.5851 | 43.5465
| 2030 | 8.631 | 8.2616 | 6.9531 | 1.9586 | 3.0278 | 13.0806 | 44.6697
| 2031 | 8.6794 | 8.1483 | 6.9708 | 2.3727 | 3.4089 | 13.5428 | 45.9511
| 2032 | 8.7268 | 8.0366 | 6.9911 | 2.8022 | 3.7901 | 13.9374 | 47.1819
| 2033 | 8.7733 | 7.9264 | 7.0146 | 3.2434 | 4.1713 | 14.2825 | 48.3764
| 2034 | 8.8187 | 7.8177 | 7.0432 | 3.6927 | 4.5524 | 14.562 | 49.5152
Figure 4.8 Sectoral contribution to Ireland's TER in 2025 & 2034
|  | 2025 (TWh) | 2034 (TWh)
| Residential | 8.4448 | 8.8187
| Commercial | 8.7809 | 7.8177
| Industrial | 6.9468 | 7.0432
| Electric Vehicles | 0.46647 | 3.6927
| Heat Pumps | 1.2707 | 4.5524
| Data Centres & New Tech Loads | 9.4069 | 14.562
4.2.9 Peak demand forecasting – overall
Figure 4.9 Sectoral contribution to Ireland's peak demand in 2025 & 2034
|  | 2025 (MW) | 2034 (MW)
| Residential, Commercial & Industrial | 4621.3016 | 4221.8159
| Electric Vehicles | 79.4079 | 191.6436
| Heat Pumps | 287.8508 | 1031.2513
| Data Centres & New Tech Loads | 1144.6 | 1679.65
Figure 4.10 Transmission peak forecast for Ireland
|  | Historical (MW) | 2024 All Island Resource Adequacy Assessment |  |  | GCS23 (MW)
| Year |  | Low | Median | High | GCS23 Low | GCS23 Median | GCS23 High
| 2016 | 4902.9202
| 2017 | 5017.2312
| 2018 | 5126.2703
| 2019 | 5112.3603
| 2020 | 5341.0803
| 2021 | 5505.5497
| 2022 | 5466.2554 |  |  |  | 5486.5941 | 5486.5941 | 5486.5941
| 2023 | 5643.4201 | 5643.4201 | 5643.4201 | 5643.4201 | 5492.15 | 5754.4332 | 5945.5577
| 2024 |  | 5652.3797 | 5834.2506 | 5970.4893 | 5546.1412 | 5911.5324 | 6253.1778
| 2025 |  | 5735.5032 | 6019.7669 | 6276.2304 | 5590.6537 | 6079.5537 | 6500.379
| 2026 |  | 5815.1331 | 6210.6137 | 6557.5861 | 5658.6036 | 6259.6347 | 6758.6419
| 2027 |  | 5882.7836 | 6347.0493 | 6754.442 | 5734.2589 | 6391.7112 | 7017.8649
| 2028 |  | 5929.0902 | 6456.0135 | 6917.489 | 5773.0573 | 6506.7586 | 7186.3443
| 2029 |  | 5948.8634 | 6527.2062 | 7032.0121 | 5806.4593 | 6607.0078 | 7318.2204
| 2030 |  | 5975.3191 | 6608.1245 | 7141.2095 | 5862.4148 | 6737.0365 | 7464.5184
| 2031 |  | 6030.7258 | 6713.208 | 7245.366 | 5944.847 | 6895.0743 | 7641.1441
| 2032 |  | 6078.5982 | 6806.8691 | 7336.7244 | 6028.9856 | 7052.4099 | 7819.2261
| 2033 |  | 6139.4462 | 6914.9829 | 7442.4588
| 2034 |  | 6200.5158 | 7010.9674 | 7549.0341
Figure 4.11 Impact of climate variability in Ireland on peak demand
|  | Historical (MW) | 2024 All Island Resource Adequacy Assessment (MW)
| Year |  | Low | Median | High | Climate Variability of Low Scenario | Climate Variability of Median Scenario | Climate Variability of High Scenario
| 2020 | 5445.6538
| 2021 | 5617.5732
| 2022 | 5579.6354
| 2023 | 5756.8135
| 2024 |  | 5765.8573 | 5947.7282 | 6083.9669
| 2025 |  | 5848.8966 | 6133.1603 | 6389.6238 | 203 | 211 | 211
| 2026 |  | 5928.5265 | 6324.0071 | 6670.9794 | 210 | 225 | 231
| 2027 |  | 5996.177 | 6460.4427 | 6867.8353 | 224 | 261 | 290
| 2028 |  | 6042.5678 | 6569.4911 | 7030.9666 | 250 | 319 | 354
| 2029 |  | 6062.2567 | 6640.5996 | 7145.4054 | 290 | 373 | 414
| 2030 |  | 6088.7125 | 6721.5179 | 7254.6029 | 329 | 432 | 508
| 2031 |  | 6144.1191 | 6826.6014 | 7358.7594 | 392 | 539 | 594
| 2032 |  | 6191.9916 | 6920.2625 | 7450.1178 | 475 | 606 | 663
| 2033 |  | 6252.8395 | 7028.3763 | 7555.8521 | 523 | 669 | 733
| 2034 |  | 6313.9092 | 7124.3607 | 7662.4275 | 570 | 733 | 846
4.2.10 Demand shape
Figure 4.12 Forecast hourly demand shape in Ireland
2024 All Island Resource Adequacy Assessment (MW)
| Hour | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| 1 | 3706.1699 | 3956.4164 | 4217.3151 | 4434.8634 | 4691.7863 | 4896.5918 | 5127.4329 | 5329.5874 | 5549.0301 | 5736.3041
| 2 | 3523.3041 | 3771.9288 | 4033.7863 | 4250.0137 | 4513.7562 | 4725.1233 | 4966.3288 | 5179.1175 | 5410.6027 | 5609.2438
| 3 | 3406.7425 | 3654.3671 | 3917.8055 | 4133.9781 | 4401.8137 | 4617.4384 | 4865.8822 | 5086.2541 | 5326.0411 | 5531.7699
| 4 | 3349.2164 | 3596.6411 | 3860.663 | 4077.1393 | 4346.9562 | 4564.5616 | 4816.7425 | 5041.0847 | 5285.1973 | 5494.5534
| 5 | 3339.1315 | 3570.9425 | 3813.0849 | 3996.8607 | 4230.6521 | 4425.1918 | 4653.8411 | 4858.8989 | 5088.5616 | 5286.5123
| 6 | 3431.2082 | 3648.8493 | 3870.063 | 4024.3607 | 4224.4137 | 4395.8603 | 4598.2658 | 4779.6831 | 4988.5726 | 5168.1863
| 7 | 3764.0822 | 3969.4767 | 4169.1123 | 4299.2623 | 4466.6658 | 4612.0082 | 4781.3699 | 4930.8497 | 5109.1753 | 5261.8904
| 8 | 4242.1425 | 4433.9863 | 4603.7452 | 4706.2377 | 4829.0192 | 4939.4767 | 5064.7589 | 5172.7596 | 5310.9397 | 5429.8082
| 9 | 4553.8849 | 4741.8959 | 4898.8795 | 4995.7186 | 5100.8356 | 5199.1452 | 5306.5863 | 5397.0956 | 5516.7562 | 5619.9178
| 10 | 4683.6411 | 4869.7726 | 5020.7808 | 5113.9973 | 5210.3205 | 5302.937 | 5402.4603 | 5485.3251 | 5597.1562 | 5693.7507
| 11 | 4777.7945 | 4970.9425 | 5131.9342 | 5247.7459 | 5366.074 | 5465.9562 | 5570.1288 | 5655.276 | 5765.4274 | 5860.4548
| 12 | 4802.1918 | 4992.2685 | 5150.3205 | 5264.8333 | 5382.3918 | 5479.0548 | 5579.6027 | 5661.6311 | 5769.0384 | 5861.5479
| 13 | 4805.0822 | 4993.5753 | 5150.2959 | 5263.5956 | 5380.2685 | 5475.9616 | 5575.7562 | 5657.1175 | 5764.1616 | 5856.3945
| 14 | 4750.2 | 4937.9397 | 5094.8027 | 5205.1093 | 5320.589 | 5417.4603 | 5519.7644 | 5603.959 | 5714.4658 | 5809.7918
| 15 | 4695.5233 | 4883.6082 | 5042.1096 | 5152.5956 | 5270.4712 | 5369.3918 | 5474.9342 | 5562.3005 | 5676.5068 | 5774.9863
| 16 | 4708.5479 | 4896.6603 | 5054.6712 | 5164.9699 | 5281.9973 | 5380.6603 | 5485.5452 | 5572.2896 | 5685.6466 | 5783.5644
| 17 | 4818.5288 | 4996.2493 | 5136.3041 | 5223.3306 | 5311.3342 | 5394.2466 | 5481.863 | 5553.571 | 5654.5315 | 5742.0164
| 18 | 4924.6055 | 5075.2192 | 5187.0877 | 5245.9536 | 5303.6329 | 5364.2411 | 5457.3096 | 5534.4235 | 5639.1726 | 5729.7781
| 19 | 4938.8685 | 5093.6685 | 5207.6493 | 5266.276 | 5320.4877 | 5383.611 | 5478.8301 | 5557.2896 | 5662.5753 | 5753.4466
| 20 | 4839.2356 | 4998.9315 | 5119.989 | 5184.7678 | 5247.0904 | 5318.2795 | 5423.1836 | 5510.6148 | 5624.4877 | 5723.0904
| 21 | 4788.4685 | 4993.5151 | 5165.4849 | 5290.5027 | 5414.126 | 5528.2301 | 5647.9233 | 5746.1475 | 5867.0055 | 5969.9836
| 22 | 4518.7836 | 4729.5288 | 4914.7425 | 5047.4481 | 5188.0548 | 5315.5781 | 5453.4575 | 5569.3661 | 5708.2795 | 5827.0164
| 23 | 4144.9068 | 4361.3863 | 4561.8986 | 4701.4863 | 4861.126 | 5005.4712 | 5167.2712 | 5307.0301 | 5471.8548 | 5613.874
| 24 | 3884.3616 | 4104.0384 | 4314.2986 | 4460.0273 | 4632.874 | 4787.1534 | 4963.1151 | 5117.6858 | 5297.9452 | 5453.2329
Figure 4.13 Electric vehicle charging profiles
| Hour | Simple | Smart
| 0 | 3.323% | 10.5%
| 1 | 2.169% | 10.5%
| 2 | 1.327% | 10.5%
| 3 | 0.8442% | 7.6%
| 4 | 0.6273% | 5%
| 5 | 0.5839% | 3%
| 6 | 0.8572% | 1%
| 7 | 2.01% | 1%
| 8 | 4.292% | 1%
| 9 | 5.383% | 3%
| 10 | 4.249% | 3%
| 11 | 3.541% | 3%
| 12 | 3.455% | 2.8%
| 13 | 3.679% | 2.8%
| 14 | 3.489% | 2.8%
| 15 | 3.677% | 1%
| 16 | 4.99% | 1%
| 17 | 6.708% | 1%
| 18 | 8.671% | 1.4%
| 19 | 9.098% | 4%
| 20 | 8.426% | 4.3%
| 21 | 7.341% | 4.5%
| 22 | 6.276% | 4.7%
| 23 | 4.984% | 10.6%
Data Centre Demand
|  | Historical (MW) | 2024 All Island Resource Adequacy Assessment (MW)
| Year |  | Low | Median | High
| 2016 | 134.1
| 2017 | 174.4
| 2018 | 256.24
| 2019 | 319
| 2020 | 409.7759
| 2021 | 490.1
| 2022 | 600.5
| 2023 | 717
| 2024 |  | 769.2 | 843 | 945.5
| 2025 |  | 816.95 | 942.6 | 1140.25
| 2026 |  | 855.3 | 1030.45 | 1287.45
| 2027 |  | 892.05 | 1097.65 | 1399.65
| 2028 |  | 928.05 | 1161.85 | 1504.05
| 2029 |  | 962.8 | 1219.35 | 1593.3
| 2030 |  | 996.55 | 1275.3 | 1664.5
| 2031 |  | 1028.8 | 1325.15 | 1700.5
| 2032 |  | 1059.55 | 1365.65 | 1724.18
| 2033 |  | 1087.05 | 1404.15 | 1745.68
| 2034 |  | 1113.8 | 1429.65 | 1767.18
*Note, for the purposes of forecasting, the assessment assumes unity power factor (1 MVA = 1 MW)

## Demand - NI
Demand Forecast for Northern Ireland
4.3.4 Electrification of heat and transport
Table 4.6 Number of electric vehicles and heat pump installations included in the low, median, and high demand forecast
|  | Low |  | Median |  | High
|  | Electric Vehicles | Heat Pump Installations | Electric Vehicles | Heat Pump Installations | Electric Vehicles | Heat Pump Installations
| 2025 | 73000 | 15000 | 100000 | 22000 | 101000 | 25000
| 2030 | 250000 | 80000 | 300000 | 120000 | 320000 | 140000
4.3.5 Total Electricity Requirement forecast
Figure 4.14 Northern Ireland TER forecast
| Year | Historical (TWh) | GCS23 Median (TWh) | Low (TWh) | Median (TWh) | High (TWh)
| 2017 | 8.75
| 2018 | 8.95
| 2019 | 8.68
| 2020 | 8.28
| 2021 | 8.53
| 2022 | 8.33 | 8.33
| 2023 | 8.09 | 8.41 | 8.09 | 8.09 | 8.09
| 2024 |  | 8.62 | 7.95 | 8.21 | 8.53
| 2025 |  | 8.88 | 8.02 | 8.33 | 8.68
| 2026 |  | 9.16 | 8.14 | 8.57 | 8.94
| 2027 |  | 9.66 | 8.34 | 9.05 | 9.49
| 2028 |  | 9.8 | 8.53 | 9.31 | 9.81
| 2029 |  | 9.98 | 8.72 | 9.58 | 10.15
| 2030 |  | 10.17 | 8.92 | 9.83 | 10.49
| 2031 |  | 10.43 | 9.13 | 10.11 | 10.84
| 2032 |  | 10.76 | 9.34 | 10.47 | 11.29
| 2033 |  |  | 9.56 | 10.71 | 11.61
| 2034 |  |  | 9.77 | 10.94 | 11.92
Figure 4.15 Northern Ireland TER forecast components
|  | Conventional Demand | Electric Vehicles | Heat Pumps | Data Centres & New Tech Loads
| 2024 | 7.91 | 0.18 | 0.12 | 0
| 2025 | 7.91 | 0.27 | 0.15 | 0
| 2026 | 7.89 | 0.4 | 0.28 | 0
| 2027 | 7.94 | 0.51 | 0.39 | 0.21
| 2028 | 7.99 | 0.61 | 0.51 | 0.21
| 2029 | 8.04 | 0.71 | 0.61 | 0.23
| 2030 | 8.09 | 0.78 | 0.71 | 0.25
| 2031 | 8.14 | 0.89 | 0.82 | 0.27
| 2032 | 8.19 | 0.98 | 0.93 | 0.38
| 2033 | 8.24 | 1.06 | 1.03 | 0.38
| 2034 | 8.29 | 1.14 | 1.14 | 0.38
Table 4.7 Low, median and high Total Electricity Requirement key assumption differences
|  |  | Low | Median | High
| Number of Electric Vehicles |  | NIEN RP7 Projections | NIEN RP7 Projections | NIEN RP7 Projections
| Number of Heat Pumps |  | NIEN RP7 Projections | NIEN RP7 Projections | NIEN RP7 Projections
| Data Centre and New Technology Loads |  | None | Median Ramp | High Ramp
| Economic Growth Projection |  | Oxford Economics Ten Year Forecast Less 1% | Oxford Economics Ten Year Forecast | Oxford Economics Ten Year Forecast Plus 1%
4.3.6 Peak demand forecasting
Figure 4.16 ACS transmission peak forecasts for Northern Ireland
| Year | Historical (GW) | GCS23 Median (GW) | Low (GW) | Median (GW) | High (GW)
| 2018 | 1.68
| 2019 | 1.71
| 2020 | 1.63
| 2021 | 1.62
| 2022 | 1.62
| 2023 | 1.57 | 1.56
| 2024 |  | 1.6 | 1.45 | 1.56 | 1.67
| 2025 |  | 1.64 | 1.46 | 1.57 | 1.69
| 2026 |  | 1.68 | 1.49 | 1.63 | 1.75
| 2027 |  | 1.75 | 1.53 | 1.71 | 1.83
| 2028 |  | 1.78 | 1.57 | 1.76 | 1.89
| 2029 |  | 1.8 | 1.6 | 1.8 | 1.94
| 2030 |  | 1.83 | 1.63 | 1.84 | 1.98
| 2031 |  | 1.85 | 1.66 | 1.88 | 2.04
| 2032 |  | 1.9 | 1.69 | 1.91 | 2.11
| 2033 |  |  | 1.72 | 1.96 | 2.16
| 2034 |  |  | 1.75 | 2 | 2.21
Table 4.8 Low, median and high peak demand key assumption differences
|  |  | Low | Median | High
| Number of Electric Vehicles |  | NIEN RP7 Projections | NIEN RP7 Projections | NIEN RP7 Projections
| Number of Heat Pumps |  | NIEN RP7 Projections | NIEN RP7 Projections | NIEN RP7 Projections
| Data Centre and New Technology Loads |  | None | Median Ramp | High Ramp
| Economic Growth Projection |  | Oxford Economics Ten Year Forecast Less 1% | Oxford Economics Ten Year Forecast | Oxford Economics Ten Year Forecast Plus 1%
| Temperature |  | One in 35 Year Mild | 35 Year Average | One in 35 Year Cold
Figure 4.17 Impact of demand flexibility on 2030 peak day (median scenario)
|  | EV Charging Off Peak (MW) | EV Charging No Flexibility (MW)
| 1 | 1220 | 1100
| 2 | 1200 | 1080
| 3 | 1180 | 1070
| 4 | 1170 | 1060
| 5 | 1120 | 1060
| 6 | 1100 | 1090
| 7 | 1190 | 1230
| 8 | 1400 | 1460
| 9 | 1550 | 1610
| 10 | 1610 | 1670
| 11 | 1650 | 1670
| 12 | 1630 | 1660
| 13 | 1600 | 1630
| 14 | 1560 | 1590
| 15 | 1540 | 1570
| 16 | 1590 | 1620
| 17 | 1720 | 1780
| 18 | 1870 | 1930
| 19 | 1820 | 1870
| 20 | 1750 | 1800
| 21 | 1730 | 1720
| 22 | 1630 | 1630
| 23 | 1490 | 1490
| 24 | 1330 | 1320
Figure 4.18 Impact of demand flexibility in median scenario across the study period
|  | EV Charging Off Peak (MW) | EV Charging No Flexibility (MW)
| 2024 | 1592.4 | 1591
| 2025 | 1605.6857 | 1612
| 2026 | 1669.5429 | 1679
| 2027 | 1748.6 | 1766
| 2028 | 1794.3714 | 1817
| 2029 | 1835.4571 | 1882
| 2030 | 1874.7429 | 1930
| 2031 | 1914.4286 | 1978
| 2032 | 1950.0857 | 2024
| 2033 | 1994.0857 | 2072
| 2034 | 2038.7143 | 2127

## Demand - AI
Demand Forecast for All-Island
4.4 The combined all-island forecast
Figure 4.19 Combined TER forecast for all-island system
| Year | Historical (TWh) | Low (TWh) | Median (TWh) | High (TWh) | GCS23 Median (TWh)
| 2020 | 38.9
| 2021 | 40.3
| 2022 | 41.694
| 2023 | 42.1325
| 2024 |  | 43.014 | 44.0601 | 44.8796 | 45.1026
| 2025 |  | 43.7492 | 46.0565 | 47.8583 | 46.877
| 2026 |  | 44.7348 | 48.0655 | 50.8062 | 48.7379
| 2027 |  | 45.7267 | 50.1597 | 53.5437 | 50.6937
| 2028 |  | 46.5292 | 51.6778 | 55.4922 | 52.0672
| 2029 |  | 47.3206 | 53.1309 | 57.3598 | 53.4754
| 2030 |  | 48.0904 | 54.4967 | 59.0345 | 54.8994
| 2031 |  | 49.0143 | 56.066 | 60.6764 | 56.5997
| 2032 |  | 49.9455 | 57.6504 | 62.2069 | 58.3816
| 2033 |  | 50.8707 | 59.0833 | 63.5545
| 2034 |  | 51.7893 | 60.4546 | 64.9012
Figure 4.20 TER peak for the combined all-island forecast
| Year | Historic (MW) | Low (MW) | Med (MW) | High (MW) | GCS23 (MW)
| 2020 | 6982.965
| 2021 | 7120
| 2022 | 7017.36
| 2023 | 7356.8135
| 2024 |  | 7255.8573 | 7537.7282 | 7793.9669 | 7588.2312
| 2025 |  | 7390.489 | 7719.8214 | 8055.3621 | 7795.6192
| 2026 |  | 7498.6654 | 7974.2455 | 8387.6249 | 8015.066
| 2027 |  | 7606.0192 | 8190.4617 | 8671.2137 | 8217.4145
| 2028 |  | 7688.239 | 8326.5316 | 8887.5375 | 8353.1445
| 2029 |  | 7738.726 | 8449.2195 | 9047.766 | 8484.1061
| 2030 |  | 7782.3072 | 8530.3197 | 9171.8598 | 8644.1871
| 2031 |  | 7854.5834 | 8662.3279 | 9298.7419 | 8822.4957
| 2032 |  | 7915.8607 | 8787.2956 | 9425.3476 | 9029.6742
| 2033 |  | 7982.6754 | 8900.5816 | 9560.2551
| 2034 |  | 8057.9008 | 9028.6166 | 9703.8278

## Generation - All Island
Generation - All Island
5.1 Introduction
Figure 5.1 Age breakdown of dispatchable plant for the All-Island system operational in 2025
| Conventional |  |  | Hydro
| Year | Capacity (MW) |  | Year | Capacity (MW)
| < 10 years | 971 |  | < 10 years | 0
| 10 - 19 years | 2392 |  | 10 - 19 years | 292
| 20 - 29 years | 2708 |  | 292 - 92 years | 92
| > 29 years | 497 |  | > 79 years | 124
5.4.1 North South Tie Line
Table 5.5 North South Tie Line net transfer capacity
| N > S Capacity (MW) | S > N Capacity (MW) | Description
| 300 | 300 | Existing North South tie line. Included in all years of the study horizon for the jurisdictional core adequacy assessments.
| 900 | 950 | New North South Tie Line. Included from 2027 for the All-Island assessment.
5.4.2 HVDC interconnection from the all-island system to Great Britain and France
Table 5.6 HVDC net transfer capacity (MW) assumptions
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
| Moyle | 450 | 450 | 450 | 500 | 500 | 500
| EWIC | 500 | 500 | 500 | 500 | 500 | 500
| Greenlink | 500 | 500 | 500 | 500 | 500 | 500
| Celtic | 0 | 0 | 700 | 700 | 700 | 700
5.4.3 Further interconnection
Table 5.7 Further interconnection projects
| Project | Description | Project Promoters Target Commissioning Year | Assumed Net Transfer Capacity (MW)
| LirIC | Interconnector between Northern Ireland and Scotland | 2029 | 700
| MARES Connect | Interconnector between Ireland and Wales | 2029 | 750

## Generation - Conventional IE
Conventional Generation - IE
5.3.1 Conventional generation portfolio in Ireland
Figure 5.2 Conventional generation portfolio assumed in Ireland
|  | 2024 | 2034
| Gas Turbine (MW) | 4350 | 5770
| Steam Turbine (MW) | 750
Table 5.1 Ireland assumptions for new conventional plant capacities in adequacy studies (rated MW). This risk adjusted view is based on plant delivering early, delivering late, or not delivering. For reference, the capacity successful in capacity auctions that has not received a termination notice is also presented. Note all values are rounded to the nearest 10 MW and capacity is presented as capacity commissioning during the calendar year.
|  | 2025 | 2026 | 2027 | 2028 | Total
| Total Successful in Capacity Auctions | 980 | 120 | 1270 | 60 | 2430
| Core Scenario Risk Adjusted View of New Capacity Delivery | 530 | 290 | 760 | 60 | 1640
Table 5.2 Assumptions for conventional plant changes in Ireland
| Plant | Units | Export Capacity (MW) | Expected Closure Date | Comment
| Aghada | AT1 | 90 | - | Previously assumed to close at the end of 2023, however, is now assumed to be operational for the entire study period as the closure notice for the unit has been withdrawn.
| Moneypoint | MP1 | 250 | End of June 2025 | Following submission of a closure notice and the outcome of the 2024/2025 T-1 Capacity Auction, these units are considered as in-market resources until the end of June 2025, at which point they will no longer be eligible for capacity payments due to CO2 limits.
|  | MP2 | 250 |  | EirGrid notes that these units will be retained beyond this date for security of supply purposes. However, this is considered a mitigating measure and not part of the core scenario.
|  | MP3 | 250 |  | MP2 is now running on Heavy Fuel Oil (HFO) with a capacity of 250 MW. The declared availability of MP1 and MP3 has declined recently and is now on average 250 MW.
| Edenderry | ED3 | 58 | N/A | Awarded capacity in the 2025/2026 T-4 capacity auction to switch fuel from Distillate Oil to Gas
|  | ED5 | 58 | N/A | Awarded capacity in the 2025/2026 T-4 capacity auction to switch fuel from Distillate Oil to Gas
5.3.3 Operational restrictions
Table 5.3 Capacity (MW) assumed to be subject to run hour limits in Ireland
| Run Hour Restriction | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
| 500 hours | 270 | 390 | 840 | 840 | 730 | 730
| 1500 hours | 210 | 210 | 210 | 210 | 210 | 210

## Generation - Conventional NI
Conventional Generation - NI
5.3.2 Conventional generation portfolio in Northern Ireland
Figure 5.3 Conventional generation portfolio assumed in Northern Ireland
Full horizon (MW)
| Gas Turbine | 2106
5.3.3 Operational restrictions
Table 5.4 Capacity (MW) assumed to be subject to run hour limits in Northern Ireland
| Run Hour Restriction | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
| 500 hours | 310 | 310 | 310 | 310 | 310 | 310
| 1500 hours | 700 | 700 | 700 | 700 | 700 | 700

## Generation - Renewable IE
Renewable Generation - IE
5.5.1 Variable generation portfolio in Ireland
Table 5.8 Climate Action Plan renewable targets in Ireland
|  | 2025 Target | 2030 Target
| Onshore Wind | 6 GW | 9 GW
| Offshore Wind | - | At least 5 GW
| Solar | Up to 5 GW | 8 GW
Figure 5.4 Assumed growth of variable generation capacity in Ireland
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Offshore Wind | 0.025 | 0.025 | 0.025 | 0.025 | 0.025 | 1.354 | 1.952 | 2.516 | 3.118 | 3.727
| Onshore Wind | 5.418 | 5.744 | 6.068 | 6.441 | 6.811 | 7.13 | 7.533 | 7.939 | 8.35 | 8.77
| Solar | 2.507 | 3.261 | 4.014 | 4.768 | 5.521 | 6.279 | 6.883 | 7.476 | 8.061 | 8.639
| Hydro | 0.216 | 0.216 | 0.216 | 0.216 | 0.216 | 0.216 | 0.216 | 0.216 | 0.216 | 0.216

## Generation - Renewable NI
Renewable Generation - NI
5.5.2 Variable generation portfolio in Northern Ireland
Figure 5.5 Assumed growth of variable generation capacity in Northern Ireland
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Offshore Wind | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| Onshore Wind | 1.435 | 1.485 | 1.535 | 1.635 | 1.81 | 1.985 | 2.16 | 2.335 | 2.51 | 2.685
| Solar | 0.25 | 0.3 | 0.35 | 0.4 | 0.45 | 0.5 | 0.55 | 0.6 | 0.65 | 0.7

## Generation - Non-Conventional
Non-Conventional Generation
5.6.1 Energy storage portfolio in Ireland
Table 5.9 Ireland energy storage capacity (MW)
| Duration | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
| <= 1 Hour | 440 | 460 | 460 | 460 | 460 | 460
| 1-2 Hours | 290 | 290 | 290 | 370 | 370 | 370
| > 2 Hours | 380 | 400 | 540 | 540 | 540 | 540
| Total | 1110 | 1150 | 1290 | 1370 | 1370 | 1370
Table 5.10 Ireland energy storage (MWh)
| Duration | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
| <= 1 Hour | 270 | 280 | 280 | 280 | 280 | 280
| 1-2 Hours | 570 | 570 | 570 | 690 | 690 | 690
| > 2 Hours | 1780 | 1850 | 2360 | 2360 | 2360 | 2360
| Total | 2620 | 2700 | 3210 | 3330 | 3330 | 3330
5.6.2 Energy storage portfolio in Northern Ireland
Table 5.11 Northern Ireland energy storage capacity (MW)
| Duration | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
| <= 1 Hour | 200 | 200 | 200 | 200 | 200 | 200
| 1-2 Hours | 0 | 0 | 0 | 0 | 0 | 0
| > 2 Hours | 0 | 0 | 0 | 0 | 0 | 0
| Total | 200 | 200 | 200 | 200 | 200 | 200
Table 5.12 Northern Ireland energy storage (MWh)
| Duration | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
| <= 1 Hour | 140 | 140 | 140 | 140 | 140 | 140
| 1-2 Hours | 0 | 0 | 0 | 0 | 0 | 0
| > 2 Hours | 0 | 0 | 0 | 0 | 0 | 0
| Total | 140 | 140 | 140 | 140 | 140 | 140
5.7.1 Demand Side Unit portfolio in Ireland
Table 5.13 Ireland DSU capacity (MW)
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
| Run Hour Limited | 660 | 540 | 510 | 550 | 550 | 550
| Non-Run Hour Limited | 170 | 150 | 210 | 310 | 310 | 310
Table 5.14 Ireland DSU run hour restriction (hours)
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
| Daily Activation Limit | 2 | 2 | 3 | 3 | 3 | 3
5.7.2 Demand Side Unit portfolio in Northern Ireland
Table 5.15 Northern Ireland DSU capacity (MW)
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
| Run Hour Limited | 200 | 220 | 100 | 160 | 160 | 160
| Non-Run Hour Limited | 0 | 0 | 30 | 10 | 10 | 10
Table 5.16 Northern Ireland DSU run hour restriction (hours)
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
| Daily Activation Limit | 5 | 5 | 5 | 5 | 5 | 5
Table 5.17 Northern Ireland AGU capacity (MW)
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030
| AGU | 79 | 79 | 79 | 79 | 79 | 79

## Generation - Availability
Generation Plant Availability
Technology Classes
Table 5.18 Summary of technology class availability statistics
| Technology Category | Mean Forced Outage Probability (%) | Mean Scheduled Outage Rate (%) | Mean Scheduled Outage Duration (hours) | Annual Availability (%)
| DSU | - | - | - | 28.4
| DSU Run Hour Limited | - | - | - | 28.2
| Gas Turbine | 8.9 | 5.3 | 470 | 85.8
| Hydro | 10.9 | 5.4 | 470 | 83.7
| Steam Turbine | 11.3 | 9.4 | 820 | 79.3
| Interconnector | 4.5 | 3.8 | 340 | 91.7
| Pumped Hydro Storage | 2.7 | 7.4 | 650 | 89.9
| System Wide | 19.2 | 7.7 | 680 | 73.1
5.9.1 Historic plant availability
Figure 5.6 All-island average annual generation capacity availability for the past 10 years (excluding DSU)
| Year | Availability | 2018 5-Year Average | 2023 5-Year Average | 2023 Average (Retired Plant Removed)
| 2014 | 85.1 | 87.84
| 2015 | 89.5
| 2016 | 89.7
| 2017 | 90.2
| 2018 | 84.7
| 2019 | 79.8 |  | 76.8 | 84.2
| 2020 | 81.1
| 2021 | 71.4
| 2022 | 74.4
| 2023 | 77.3
Figure 5.7 Average annual conventional generation capacity forced and scheduled outage rates in Ireland for the past 10 years
| Year | Forced Outage Rate (IE) (%) | 2018 5-Year Average | 2023 5-Year Average |  | Year | Scheduled Outage Rate (IE) (%) | 2018 5-Year Average | 2023 5-Year Average
| 2014 | 6.8 | 5.22 |  |  | 2014 | 8 | 6.02
| 2015 | 2.9 |  |  |  | 2015 | 4.9
| 2016 | 4.1 |  |  |  | 2016 | 5.7
| 2017 | 5.5 |  |  |  | 2017 | 3.4
| 2018 | 6.8 |  |  |  | 2018 | 8.1
| 2019 | 10.3 |  | 16.14 |  | 2019 | 9.3 |  | 6.5
| 2020 | 12.6 |  |  |  | 2020 | 5.8
| 2021 | 21.9 |  |  |  | 2021 | 7.8
| 2022 | 18.1 |  |  |  | 2022 | 6.5
| 2023 | 17.8 |  |  |  | 2023 | 3.1
Figure 5.8 Average annual conventional generation capacity forced and scheduled outage rates in Northern Ireland for the past 10 years
| Year | Forced Outage Rate (IE) (%) | 2018 5-Year Average | 2023 5-Year Average |  | Year | Scheduled Outage Rate (IE) (%) | 2018 5-Year Average | 2023 5-Year Average
| 2014 | 9.6 | 8.16 |  |  | 2014 | 4.9 | 3.18
| 2015 | 10.3 |  |  |  | 2015 | 4
| 2016 | 4.6 |  |  |  | 2016 | 4.4
| 2017 | 6.4 |  |  |  | 2017 | 1.1
| 2018 | 9.9 |  |  |  | 2018 | 1.5
| 2019 | 10.5 |  | 12.68 |  | 2019 | 7.8 |  | 7.08
| 2020 | 9.7 |  |  |  | 2020 | 6.2
| 2021 | 12.7 |  |  |  | 2021 | 8.7
| 2022 | 13.9 |  |  |  | 2022 | 8
| 2023 | 16.6 |  |  |  | 2023 | 4.7
Figure 5.9 Ireland and Northern Ireland conventional generation capacity availability across the last 5 years
| Date | Ireland | Northern Ireland
| 2014-01-01 | 87.4106 | 89.6437
| 2014-02-01 | 86.9706 | 89.5818
| 2014-03-01 | 87.3456 | 88.5638
| 2014-04-01 | 87.1262 | 87.2384
| 2014-05-01 | 86.59 | 86.9698
| 2014-06-01 | 85.9043 | 87.216
| 2014-07-01 | 85.3719 | 87.5872
| 2014-08-01 | 85.3313 | 87.3543
| 2014-09-01 | 84.7814 | 86.2339
| 2014-10-01 | 84.2184 | 85.8895
| 2014-11-01 | 84.1348 | 85.7819
| 2014-12-01 | 85.138 | 85.0584
| 2015-01-01 | 86.3639 | 85.6
| 2015-02-01 | 86.9313 | 85.489
| 2015-03-01 | 87.6114 | 85.8782
| 2015-04-01 | 88.5203 | 86.2004
| 2015-05-01 | 89.5091 | 85.4349
| 2015-06-01 | 90.6502 | 85.3642
| 2015-07-01 | 91.1194 | 85.1724
| 2015-08-01 | 90.9593 | 84.8501
| 2015-09-01 | 91.511 | 84.7482
| 2015-10-01 | 92.2731 | 83.954
| 2015-11-01 | 91.8568 | 83.9377
| 2015-12-01 | 91.6963 | 84.0648
| 2016-01-01 | 91.5092 | 83.9652
| 2016-02-01 | 91.469 | 84.2295
| 2016-03-01 | 91.2074 | 84.962
| 2016-04-01 | 90.8919 | 86.0398
| 2016-05-01 | 90.6191 | 86.6182
| 2016-06-01 | 89.5453 | 86.2096
| 2016-07-01 | 89.7352 | 86.6565
| 2016-08-01 | 90.1774 | 86.6489
| 2016-09-01 | 90.2497 | 86.4056
| 2016-10-01 | 89.7966 | 87.3674
| 2016-11-01 | 90.368 | 88.2747
| 2016-12-01 | 90.0052 | 88.8274
| 2017-01-01 | 90.2413 | 88.4642
| 2017-02-01 | 90.1096 | 88.2439
| 2017-03-01 | 90.2463 | 88.2932
| 2017-04-01 | 90.2864 | 88.1859
| 2017-05-01 | 90.6362 | 88.6377
| 2017-06-01 | 91.2506 | 89.6891
| 2017-07-01 | 91.093 | 89.6217
| 2017-08-01 | 91.0197 | 90.315
| 2017-09-01 | 90.5103 | 90.5719
| 2017-10-01 | 90.5686 | 90.7769
| 2017-11-01 | 89.9365 | 90.698
| 2017-12-01 | 90.1541 | 90.4019
| 2018-01-01 | 89.943 | 90.8931
| 2018-02-01 | 89.5534 | 91.365
| 2018-03-01 | 88.9535 | 91.3749
| 2018-04-01 | 88.4437 | 90.9003
| 2018-05-01 | 88.0412 | 90.7543
| 2018-06-01 | 87.6867 | 89.5412
| 2018-07-01 | 87.5296 | 88.6745
| 2018-08-01 | 87.4208 | 87.7706
| 2018-09-01 | 87.9965 | 88.1567
| 2018-10-01 | 86.9049 | 87.7612
| 2018-11-01 | 85.9045 | 87.0248
| 2018-12-01 | 84.0721 | 86.6411
| 2019-01-01 | 82.3531 | 85.1516
| 2019-02-01 | 81.5589 | 83.9705
| 2019-03-01 | 80.7477 | 83.0359
| 2019-04-01 | 80.1777 | 82.1799
| 2019-05-01 | 79.6933 | 80.9664
| 2019-06-01 | 79.1679 | 80.8428
| 2019-07-01 | 78.5145 | 80.5854
| 2019-08-01 | 77.5933 | 80.0822
| 2019-09-01 | 76.6255 | 80.2454
| 2019-10-01 | 77.0196 | 80.6793
| 2019-11-01 | 78.2481 | 81.0417
| 2019-12-01 | 79.4302 | 81.1489
| 2020-01-01 | 80.441 | 81.824
| 2020-02-01 | 80.9039 | 82.1911
| 2020-03-01 | 81.2482 | 82.6305
| 2020-04-01 | 81.4834 | 83.7498
| 2020-05-01 | 81.8459 | 84.7787
| 2020-06-01 | 82.047 | 85.7416
| 2020-07-01 | 81.9002 | 86.3933
| 2020-08-01 | 81.8655 | 86.0752
| 2020-09-01 | 81.8774 | 85.6609
| 2020-10-01 | 81.6572 | 83.9092
| 2020-11-01 | 81.2616 | 82.235
| 2020-12-01 | 80.6556 | 82.5914
| 2021-01-01 | 80.2008 | 82.9102
| 2021-02-01 | 79.0074 | 82.821
| 2021-03-01 | 78.2546 | 82.4517
| 2021-04-01 | 77.0244 | 82.0896
| 2021-05-01 | 75.03 | 81.2877
| 2021-06-01 | 73.6099 | 79.7651
| 2021-07-01 | 72.3371 | 79.0364
| 2021-08-01 | 71.4129 | 79.956
| 2021-09-01 | 70.0051 | 79.0889
| 2021-10-01 | 69.3956 | 79.1568
| 2021-11-01 | 68.7968 | 79.3701
| 2021-12-01 | 69.4139 | 78.4462
| 2022-01-01 | 69.9054 | 78.0907
| 2022-02-01 | 70.984 | 78.1604
| 2022-03-01 | 71.1495 | 78.5925
| 2022-04-01 | 71.5807 | 77.8883
| 2022-05-01 | 72.0374 | 77.1539
| 2022-06-01 | 72.4127 | 77.3757
| 2022-07-01 | 72.8021 | 76.8017
| 2022-08-01 | 73.2503 | 75.164
| 2022-09-01 | 74.1702 | 75.0891
| 2022-10-01 | 74.1344 | 75.27
| 2022-11-01 | 74.2666 | 75.3662
| 2022-12-01 | 74.1718 | 75.4126
| 2023-01-01 | 73.9147 | 75.1135
| 2023-02-01 | 73.6064 | 74.8625
| 2023-03-01 | 73.784 | 74.3281
| 2023-04-01 | 74.2467 | 74.8395
| 2023-05-01 | 74.9315 | 74.159
| 2023-06-01 | 75.2174 | 73.5454
| 2023-07-01 | 75.578 | 73.1066
| 2023-08-01 | 75.8854 | 72.865
| 2023-09-01 | 75.7464 | 73.1456
| 2023-10-01 | 76.6001 | 74.5555
| 2023-11-01 | 77.3227 | 75.9535
| 2023-12-01 | 77.6838 | 76.8553
| 2024-01-01 | 78.0713 | 77.8037
Figure 5.10 All-Island demand side unit monthly availability for 2022 and 2023 calendar years
| Year | DSU Monthly Availability | DSU Awarded Capacity (De-rated) | DSU Monthly Availability
| 2022-01-01 | 161.6 | 471 | 731
| 2022-02-01 | 185.7 | 471 | 731
| 2022-03-01 | 176.9 | 471 | 731
| 2022-04-01 | 197.4 | 471 | 731
| 2022-05-01 | 195.9 | 471 | 731
| 2022-06-01 | 197.4 | 471 | 731
| 2022-07-01 | 156.4 | 471 | 731
| 2022-08-01 | 160.8 | 471 | 731
| 2022-09-01 | 182.8 | 471 | 731
| 2022-10-01 | 184.2 | 471 | 731
| 2022-11-01 | 184.2 | 471 | 731
| 2022-12-01 | 145.5 | 471 | 731
| 2023-01-01 | 159.4 | 471 | 731
| 2023-02-01 | 170.3 | 471 | 731
| 2023-03-01 | 184.2 | 471 | 731
| 2023-04-01 | 166.7 | 471 | 731
| 2023-05-01 | 198.8 | 471 | 731
| 2023-06-01 | 186.4 | 471 | 731
| 2023-07-01 | 187.1 | 471 | 731
| 2023-08-01 | 167.4 | 471 | 731
| 2023-09-01 | 177.6 | 471 | 731
| 2023-10-01 | 162.3 | 471 | 731
| 2023-11-01 | 138.2 | 471 | 731
| 2023-12-01 | 131.6 | 471 | 731

## Adequacy
Adequacy
6.1 Introduction
Table 6.1 LOLE standards
| Area | LOLE Standard (hours)
| All-Island SEM | 6.5*
| Ireland | 3*
| Northern Ireland | 4.9
* Note this is a change from GCS 2023-2032 where the LOLE standard for the All-Island SEM and Ireland was 8 hours
6.4 Ireland adequacy analysis
Figure 6.2 Base and Secure surplus/deficit results for Ireland
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| LOLE Base | 33.1 | 28.8 | 5 | 3.2 | 3 | 2.3 | 1.9 | 2.4 | 3.8 | 3.6
| LOLE Secure | 65.4 | 67.4 | 16.9 | 11.3 | 15.7 | 12.3 | 15.3 | 21 | 32.3 | 40
| 3 hour LOLE Standard | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Figure 6.3 Distribution of LOLE Base results for the Ireland median demand scenario where each low/mid/high band represents 1/3rd of the 35 climate year results (includes reserves)
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Minimum | 12.1 | 11.5 | 0.4 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0.5
| Low | 12.8 | 9.2 | 1.5 | 1.9 | 1.3 | 0.8 | 0.9 | 1.4 | 2 | 1.6
| Mid | 8.2 | 9.9 | 2 | 1.9 | 2 | 0.8 | 0.8 | 0.8 | 1.5 | 1.3
| High | 66.3 | 68.5 | 22.4 | 6.1 | 7.2 | 15.6 | 11.5 | 12.2 | 24.2 | 17.2
| LOLE Base | 33.1 | 28.8 | 5 | 3.2 | 3 | 2.3 | 1.9 | 2.4 | 3.8 | 3.6
Table 6.2 LOLE and EENS Base results for Ireland (includes reserves)
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| LOLE Base (hours) | 33.1 | 28.8 | 5 | 3.2 | 3 | 2.3 | 1.9 | 2.4 | 3.8 | 3.6
| EENS Base (GWh) | 10.5 | 9.8 | 2 | 1 | 1.1 | 0.9 | 0.6 | 0.8 | 1.4 | 1
Table 6.3 LOLE and EENS Base Demand Only results for Ireland (excludes reserves)
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| LOLE Base Demand Only (hours) | 12.9 | 11.7 | 1.7 | 0.7 | 0.9 | 0.7 | 0.4 | 0.5 | 1 | 0.8
| EENS Base Demand Only (GWh) | 3.4 | 3.6 | 0.5 | 0.2 | 0.3 | 0.2 | 0.1 | 0.2 | 0.4 | 0.2
Table 6.4 Average LOLE of the 3 climate years used in the surplus/deficit calculation for Ireland (includes reserves)
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| 3 Climate Year LOLE | 25.1 | 30.5 | 7.8 | 3 | 2.6 | 2.2 | 2.1 | 2.5 | 4.4 | 3.6
Figure 6.4 MW Base results for Ireland in terms of surplus (+) and deficit (-) of perfect plant
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Demand | -185 | -305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reserve | -375 | -375 | -260 | 0 | 0 | 0 | 0 | 0 | -120 | -70
| MW Base | -560 | -680 | -260 | 10 | 50 | 110 | 140 | 70 | -120 | -70
Table 6.5 MW Base results for Ireland in terms of surplus (+) and deficit (-) of perfect plant
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| MW Base | -560 | -680 | -260 | 10 | 50 | 110 | 140 | 70 | -120 | -70
Figure 6.5 Sensitivity analysis for Ireland in terms of deficit (-) of perfect plant impact
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Low Imports | -160 | -130 | -90 | -160 | -160 | -140 | -300 | -200 | -430 | -300
| 2 FR Nuclear Units Out | -120 | -120 | -170 | -230 | -200 | -150 | -170 | -150 | -220 | -190
| 4 FR Nuclear Units Out | -230 | -240 | -340 | -460 | -390 | -300 | -340 | -290 | -440 | -370
| 2001 Climate Year | -150 | -190 | -60 | -160 | -260 | -330 | -310 | -440 | -620 | -410
| Low Plant Availability | -100 | -230 | -170 | -330 | -410 | -120 | -160 | -120 | -280 | -150
Figure 6.6 Distribution of LOLE Secure results for the Ireland median demand scenario where each low/mid/high band represents 1/3rd of the 35 climate year results (includes reserves)
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Minimum | 30.6 | 26.1 | 4.1 | 3.1 | 4.6 | 2.5 | 5.6 | 4.8 | 9.6 | 12.5
| Low | 24.8 | 29.7 | 7.2 | 5.4 | 7.3 | 6.8 | 5.8 | 10.2 | 15.9 | 19.7
| Mid | 10.3 | 12.6 | 6.1 | 5 | 4.3 | 2.9 | 3.2 | 6.8 | 8.2 | 7.5
| High | 96.8 | 113.1 | 52.5 | 14.4 | 35.7 | 51.4 | 47.7 | 67.9 | 86.3 | 98.9
| LOLE Secure | 65.4 | 67.4 | 16.9 | 11.3 | 15.7 | 12.3 | 15.3 | 21 | 32.3 | 40
Table 6.6 LOLE and EENS Secure results for Ireland (includes reserves)
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| LOLE Secure (hours) | 65.4 | 67.4 | 16.9 | 11.3 | 15.7 | 12.3 | 15.3 | 21 | 32.3 | 40
| EENS Secure (GWh) | 20.5 | 21.7 | 5.7 | 3.5 | 4.9 | 4 | 4.3 | 6.4 | 10.4 | 12.7
Figure 6.7 Secure surplus/deficit results for Ireland in terms of surplus (+) and deficit (-) of perfect plant
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Demand | -335 | -455 | -5 | 0 | 0 | 0 | 0 | 0 | -165 | -175
| Reserve | -375 | -375 | -525 | -310 | -340 | -280 | -390 | -470 | -525 | -525
| TOPs | -350 | -350 | -350 | -350 | -350 | -350 | -350 | -350 | -350 | -350
| MW Secure | -1060 | -1180 | -880 | -660 | -690 | -630 | -740 | -820 | -1040 | -1050
Table 6.7 Secure surplus/deficit results for Ireland in terms of surplus (+) and deficit (-) of perfect plant
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| MW Secure | -1060 | -1180 | -880 | -660 | -690 | -630 | -740 | -820 | -1040 | -1050
Figure 6.8 Sensitivity analysis for Ireland
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Low Demand | 290 | 380 | 470 | 560 | 580 | 650 | 690 | 730 | 750 | 850
| High Demand | -230 | -360 | -410 | -450 | -500 | -510 | -490 | -460 | -480 | -460
| NTL Contract Ramp | -780 | -840 | -850 | -820 | -800 | -750 | -700 | -660 | -620 | -590
| CM Gas Delivery | 570 | 320 | 1040 | 800 | 790 | 860 | 720 | 760 | 660 | 780
| Low RES | -40 | -80 | -30 | -30 | -90 | -190 | -230 | -250 | -390 | -200
| CAP 2024 RES | 160 | 80 | 80 | 300 | 380 | 480 | 340 | 360 | 340 | 230
| LDES |  |  |  |  | 410 | 400 | 410 | 460 | 450 | 340
| Low Flexibility | -40 | -70 | -120 | -190 | -280 | -350 | -450 | -530 | -610 | -700
| High Flexibility | 40 | 20 | 60 | 110 | 100 | 210 | 160 | 230 | 290 | 360
Table 6.8 Low renewable deployment scenario (MW)
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Offshore Wind | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 400 | 850 | 1000
| Onshore Wind | 5150 | 5400 | 5600 | 5800 | 6000 | 6200 | 6500 | 6800 | 7100 | 7350
| Solar | 1800 | 2200 | 2600 | 3050 | 3450 | 3850 | 4200 | 4600 | 5000 | 5350
Table 6.9 SOEF v1.1 low emissions trajectory (MW)
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Offshore Wind | 25 | 25 | 25 | 1200 | 2865 | 5000 | 7135 | 9270 | 9270 | 9270
| Onshore Wind | 6004 | 7000 | 8200 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000 | 9000
| Solar | 4800 | 4800 | 5600 | 6500 | 7250 | 8000 | 8750 | 9500 | 9500 | 9500
Figure 6.9 Ireland adequacy position with mitigating measures
|  | 2025 |  | 2026 |  | 2027 |  | 2028 |  | 2029 | 2030
| Demand | -335 |  | -455 |  | -5 |  | 0 |  | 0 | 0
| Reserve | -375 |  | -375 |  | -525 |  | -310 |  | -340 | -280
| TOPs | -350 |  | -350 |  | -350 |  | -350 |  | -350 | -350
| MW Secure | -1060 |  | -1180 |  | -880 |  | -660 |  | -690 | -630
| Confirmed SoS Measures | 2026: -1170; 2028: -1170; 2030: -520; 2032: -520
| Possible SoS Measures | 2030: -650; 2032: -410
6.5 Northern Ireland adequacy analysis
Figure 6.10 Base and Secure surplus/deficit results for Northern Ireland
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| LOLE Base | 1.8 | 2.3 | 5.1 | 2 | 4.1 | 2.5 | 3.3 | 7.3 | 7.9 | 8.5
| LOLE Secure | 4.5 | 5.9 | 11.9 | 6.2 | 11 | 7.7 | 11.1 | 19.7 | 21.6 | 25.2
| 4.9 hour LOLE Standard | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9 | 4.9
Figure 6.11 Distribution of LOLE Base results for the Northern Ireland median demand scenario where each low/mid/high band represents 1/3rd of the 35 climate year results (includes reserves)
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Minimum | 0.3 | 0.1 | 1.1 | 0.2 | 1.9 | 0.8 | 0.6 | 2.7 | 3 | 3.3
| Low | 0.6 | 1.2 | 2.6 | 1.4 | 1.6 | 0.6 | 1.5 | 3 | 2.5 | 2.7
| Mid | 0.6 | 1.1 | 1.8 | 0.5 | 0.8 | 0.9 | 0.9 | 1.9 | 2.3 | 2.3
| High | 10.6 | 13.2 | 17.2 | 3 | 7.4 | 19.6 | 14.2 | 24.2 | 39.4 | 35.3
| LOLE Base | 1.8 | 2.3 | 5.1 | 2 | 4.1 | 2.5 | 3.3 | 7.3 | 7.9 | 8.5
Table 6.10 LOLE and EENS Base results for Northern Ireland (includes reserves)
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| LOLE Base (hours) | 1.8 | 2.3 | 5.1 | 2 | 4.1 | 2.5 | 3.3 | 7.3 | 7.9 | 8.5
| EENS Base (GWh) | 0.2 | 0.3 | 0.6 | 0.2 | 0.5 | 0.3 | 0.4 | 0.9 | 1.1 | 1.1
Table 6.11 LOLE and EENS Base Demand Only results for Northern Ireland (excludes reserves)
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| LOLE Base Demand Only (hours) | 0.8 | 1.1 | 1.4 | 0.6 | 1.3 | 0.8 | 0.9 | 2.1 | 2.6 | 2.8
| EENS Base Demand Only (GWh) | 0.09 | 0.15 | 0.2 | 0.07 | 0.15 | 0.13 | 0.12 | 0.25 | 0.37 | 0.33
Table 6.12 Average LOLE of the 3 climate years used in the surplus/deficit calculation for Northern Ireland (includes reserves)
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| 3 Climate Year LOLE | 1.4 | 3 | 4.6 | 3.9 | 3.8 | 2.4 | 4.5 | 6.3 | 6.1 | 7.5
Figure 6.12 MW Base results for Northern Ireland in terms of surplus (+) and deficit (-) of perfect plant
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reserve | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -30 | -20 | -50
| MW Base | 120 | 60 | 10 | 20 | 30 | 70 | 10 | -30 | -20 | -50
Table 6.13 MW Base results for Northern Ireland in terms of surplus (+) and deficit (-) of perfect plant
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| MW Base | 120 | 60 | 10 | 20 | 30 | 70 | 10 | -30 | -20 | -50
Figure 6.13 Sensitivity analysis for Northern Ireland in terms of deficit (-) of perfect plant impact
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Low Imports | -140 | -120 | -120 | -120 | -130 | -110 | -130 | -120 | -120 | -150
| 2 FR Nuclear Units Out | -80 | -70 | -100 | -90 | -80 | -60 | -70 | -70 | -60 | -80
| 4 FR Nuclear Units Out | -160 | -140 | -200 | -170 | -160 | -120 | -130 | -130 | -120 | -150
| 2001 Climate Year | -90 | -140 | -130 | -80 | -50 | -60 | -50 | -120 | -130 | -170
| Low Plant Availability | -10 | -120 | -50 | -150 | -110 | -110 | -70 | -80 | -70 | -70
Figure 6.14 Distribution of LOLE Secure results for the Northern Ireland median demand scenario where each low/mid/high band represents 1/3rd of the 35 climate year results (includes reserves)
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Minimum | 1.7 | 1 | 5.6 | 1.8 | 5.6 | 3.4 | 5.1 | 9.7 | 10.4 | 11.1
| Low | 1.4 | 3.1 | 4.3 | 3.2 | 4 | 2.1 | 2.5 | 5.9 | 6.3 | 8.8
| Mid | 1.8 | 2.4 | 2.8 | 1.6 | 1.8 | 1.1 | 3.3 | 4 | 4.1 | 4
| High | 13 | 19.2 | 30.7 | 11.6 | 22 | 40.3 | 41.4 | 58.7 | 79.7 | 88.4
| LOLE Secure | 4.5 | 5.9 | 11.9 | 6.2 | 11 | 7.7 | 11.1 | 19.7 | 21.6 | 25.2
Table 6.14 LOLE and EENS Secure results for Northern Ireland (includes reserves)
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| LOLE Secure (hours) | 4.5 | 5.9 | 11.9 | 6.2 | 11.0 | 7.7 | 11.1 | 19.7 | 21.6 | 25.2
| EENS Secure (GWh) | 0.5 | 0.7 | 1.6 | 0.7 | 1.4 | 1 | 1.4 | 2.8 | 3.3 | 3.7
Figure 6.15 MW Secure results for Northern Ireland in terms of surplus (+) and deficit (-) of perfect plant
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -35
| Reserve | 0 | -50 | -90 | -80 | -80 | -50 | -110 | -160 | -160 | -175
| MW Secure | 20 | -50 | -90 | -80 | -80 | -50 | -110 | -160 | -160 | -210
Table 6.15 MW Secure results for Northern Ireland in terms of surplus (+) and deficit (-) of perfect plant
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| MW Secure | 20 | -50 | -90 | -80 | -80 | -50 | -110 | -160 | -160 | -210
Figure 6.16 Sensitivity analysis for Northern Ireland
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Low Demand | 50 | 100 | 90 | 100 | 100 | 130 | 130 | 150 | 150 | 160
| High Demand | -90 | -80 | -70 | -80 | -90 | -110 | -100 | -110 | -140 | -150
| Removed ARHL | 180 | 240 | 270 | 210 | 260 | 300 | 250 | 280 | 190 | 270
| Low RES | -10 | -10 | -10 | -10 | -30 | -40 | -60 | -40 | -40 | -40
| High RES | 20 | 30 | 10 | 20 | 20 | 50 | 70 | 60 | 40 | 50
| LDES Storage |  |  |  |  | 110 | 30 | 90 | 120 | 30 | 90
| Low Flexibility | -10 | -10 | -20 | -20 | -50 | -60 | -60 | -70 | -80 | -90
Table 6.16 Northern Ireland low renewable trajectory (MW)
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Offshore Wind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 500 | 500
| Onshore Wind | 1410 | 1435 | 1460 | 1510 | 1598 | 1685 | 1773 | 1860 | 1948 | 2035
| Solar | 250 | 280 | 310 | 340 | 370 | 400 | 430 | 460 | 490 | 520
Table 6.17 Northern Ireland high renewable trajectory (MW)
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Offshore Wind | 0 | 0 | 0 | 0 | 0 | 1000 | 1000 | 1000 | 1000 | 1000
| Onshore Wind | 1540 | 1610 | 1750 | 1990 | 2170 | 2460 | 2740 | 3030 | 3030 | 3030
| Solar | 300 | 350 | 400 | 450 | 525 | 600 | 675 | 750 | 825 | 900
6.5 All-island adequacy analysis
Table 6.18 Base results for the all-island system
|  | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| LOLE Base (hours) | 4.1 | 2.6 | 3.4 | 2 | 3.5 | 2.4 | 3.7 | 2.5
| EENS Base (GWh) | 2.3 | 1 | 1.4 | 0.5 | 1.2 | 0.8 | 1.9 | 0.6
| MW Base | 240 | 280 | 260 | 380 | 320 | 250 | 130 | 140
Figure 6.17 Base scenario adequacy analysis for the all-island system in terms of surplus (+) and deficit (-) of perfect plant
|  | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reserve | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| TOPs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MW Base | 240 | 280 | 260 | 380 | 320 | 250 | 130 | 140
Table 6.19 Secure results for the all-island system
|  | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| LOLE Secure (hours) | 9.6 | 7.9 | 8.7 | 7.1 | 9.2 | 14.7 | 23.9 | 28.9
| EENS Secure (GWh) | 4.1 | 2.4 | 2.7 | 2 | 3.4 | 3.9 | 8.6 | 9.2
| MW Secure | -350 | -360 | -270 | -330 | -330 | -460 | -570 | -630
Figure 6.18 Secure scenario adequacy analysis for the all-island system in terms of surplus (+) and deficit (-) of perfect plant
|  | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Demand | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Reserve | 0 | -10 | 0 | 0 | 0 | -110 | -220 | -280
| TOPs | -350 | -350 | -270 | -330 | -330 | -350 | -350 | -350
| MW Secure | -350 | -360 | -270 | -330 | -330 | -460 | -570 | -630

## Appendix 1
Appendix 1: Demand Scenarios
Table A1.1 Demand forecast for the median scenario in calendar year format for Ireland and Northern Ireland
| Median | Calendar Year TER (TWh) | [5 empty] | TER Peak (GW) |  |  | Transmission Peak (GW)
| Year | Ireland |  | Northern Ireland |  | All-Island |  | Ireland | Northern Ireland | All-Island | Ireland | Northern Ireland | All-Island
|  | TER | % Growth | TER | % Growth | TER | % Growth
| 2023 | 34 |  | 8.09 |  | 42.1 |  | 5.76 | 1.6 | 7.36 | 5.64 | 1.57 | 7.21
| 2024 | 35.8 | 5.3% | 8.21 | 1.6% | 44.1 | 4.6% | 5.95 | 1.59 | 7.54 | 5.83 | 1.56 | 7.39
| 2025 | 37.7 | 5.2% | 8.33 | 1.4% | 46.1 | 4.5% | 6.13 | 1.61 | 7.72 | 6.02 | 1.57 | 7.57
| 2026 | 39.5 | 4.7% | 8.57 | 2.8% | 48.1 | 4.4% | 6.32 | 1.67 | 7.97 | 6.21 | 1.63 | 7.82
| 2027 | 41.1 | 4.1% | 9.05 | 5.7% | 50.2 | 4.4% | 6.46 | 1.75 | 8.19 | 6.35 | 1.71 | 8.04
| 2028 | 42.4 | 3.1% | 9.31 | 2.9% | 51.7 | 3% | 6.57 | 1.79 | 8.33 | 6.46 | 1.76 | 8.18
| 2029 | 43.5 | 2.8% | 9.58 | 2.9% | 53.1 | 2.8% | 6.64 | 1.84 | 8.45 | 6.53 | 1.8 | 8.3
| 2030 | 44.7 | 2.6% | 9.83 | 2.5% | 54.5 | 2.6% | 6.72 | 1.87 | 8.53 | 6.61 | 1.84 | 8.39
| 2031 | 46 | 2.9% | 10.11 | 2.9% | 56.1 | 2.9% | 6.83 | 1.91 | 8.66 | 6.71 | 1.88 | 8.52
| 2032 | 47.2 | 2.7% | 10.47 | 3.5% | 57.7 | 2.8% | 6.92 | 1.95 | 8.79 | 6.81 | 1.91 | 8.63
| 2033 | 48.4 | 2.5% | 10.71 | 2.3% | 59.1 | 2.5% | 7.03 | 1.99 | 8.9 | 6.91 | 1.96 | 8.76
| 2034 | 49.5 | 2.4% | 10.94 | 2.2% | 60.5 | 2.3% | 7.12 | 2.04 | 9.03 | 7.01 | 2 | 8.88
Table A1.2 Demand forecast for the low scenario in calendar year format for Ireland and Northern Ireland
| Median | Calendar Year TER (TWh) | [5 empty] | TER Peak (GW) |  |  | Transmission Peak (GW)
| Year | Ireland |  | Northern Ireland |  | All-Island |  | Ireland | Northern Ireland | All-Island | Ireland | Northern Ireland | All-Island
|  | TER | % Growth | TER | % Growth | TER | % Growth
| 2023 | 34 |  | 8.09 |  | 42.1 |  | 5.75 | 1.6 | 7.35 | 5.64 | 1.57 | 7.21
| 2024 | 35.1 | 3% | 7.95 | -1.7% | 43 | 2.1% | 5.77 | 1.49 | 7.26 | 5.65 | 1.45 | 7.11
| 2025 | 35.7 | 1.9% | 8.02 | 0.8% | 43.7 | 1.7% | 5.85 | 1.49 | 7.39 | 5.74 | 1.46 | 7.24
| 2026 | 36.6 | 2.4% | 8.14 | 1.5% | 44.7 | 2.3% | 5.93 | 1.53 | 7.5 | 5.82 | 1.49 | 7.35
| 2027 | 37.4 | 2.2% | 8.34 | 2.4% | 45.7 | 2.2% | 6 | 1.57 | 7.61 | 5.88 | 1.53 | 7.45
| 2028 | 38 | 1.6% | 8.53 | 2.3% | 46.5 | 1.8% | 6.04 | 1.61 | 7.69 | 5.93 | 1.57 | 7.54
| 2029 | 38.6 | 1.6% | 8.72 | 2.3% | 47.3 | 1.7% | 6.06 | 1.64 | 7.74 | 5.95 | 1.6 | 7.59
| 2030 | 39.2 | 1.5% | 8.92 | 2.2% | 48.1 | 1.6% | 6.09 | 1.66 | 7.78 | 5.98 | 1.63 | 7.64
| 2031 | 39.9 | 1.8% | 9.13 | 2.3% | 49 | 1.9% | 6.14 | 1.7 | 7.85 | 6.03 | 1.66 | 7.71
| 2032 | 40.6 | 1.8% | 9.34 | 2.3% | 49.9 | 1.9% | 6.19 | 1.73 | 7.92 | 6.08 | 1.69 | 7.76
| 2033 | 41.3 | 1.7% | 9.56 | 2.3% | 50.9 | 1.9% | 6.25 | 1.76 | 7.98 | 6.14 | 1.72 | 7.84
| 2034 | 42 | 1.7% | 9.77 | 2.3% | 51.8 | 1.8% | 6.31 | 1.79 | 8.06 | 6.2 | 1.75 | 7.9
Table A1.3 Demand forecast for the high scenario in calendar year format for Ireland and Northern Ireland
| Median | Calendar Year TER (TWh) | [5 empty] | TER Peak (GW) |  |  | Transmission Peak (GW)
| Year | Ireland |  | Northern Ireland |  | All-Island |  | Ireland | Northern Ireland | All-Island | Ireland | Northern Ireland | All-Island
|  | TER | % Growth | TER | % Growth | TER | % Growth
| 2023 | 34 |  | 8.1 |  | 42.1 |  | 5.76 | 1.6 | 7.36 | 5.64 | 1.57 | 7.21
| 2024 | 36.4 | 6.8% | 8.53 | 5.2% | 44.9 | 6.5% | 6.08 | 1.71 | 7.79 | 5.97 | 1.67 | 7.65
| 2025 | 39.2 | 7.8% | 8.68 | 1.8% | 47.9 | 6.6% | 6.39 | 1.73 | 8.06 | 6.28 | 1.69 | 7.9
| 2026 | 41.9 | 6.9% | 8.94 | 3% | 50.8 | 6.2% | 6.67 | 1.78 | 8.39 | 6.56 | 1.75 | 8.23
| 2027 | 44.1 | 5.2% | 9.49 | 6.2% | 53.5 | 5.4% | 6.87 | 1.87 | 8.67 | 6.75 | 1.83 | 8.52
| 2028 | 45.7 | 3.7% | 9.81 | 3.3% | 55.5 | 3.6% | 7.03 | 1.92 | 8.89 | 6.92 | 1.89 | 8.74
| 2029 | 47.2 | 3.3% | 10.15 | 3.5% | 57.4 | 3.4% | 7.15 | 1.98 | 9.05 | 7.03 | 1.94 | 8.89
| 2030 | 48.5 | 2.8% | 10.49 | 3.3% | 59 | 2.9% | 7.25 | 2.02 | 9.17 | 7.14 | 1.98 | 9.03
| 2031 | 49.8 | 2.6% | 10.84 | 3.4% | 60.7 | 2.8% | 7.36 | 2.08 | 9.3 | 7.25 | 2.04 | 9.16
| 2032 | 50.9 | 2.2% | 11.29 | 4.1% | 62.2 | 2.5% | 7.45 | 2.14 | 9.43 | 7.34 | 2.11 | 9.27
| 2033 | 51.9 | 2% | 11.61 | 2.8% | 63.6 | 2.2% | 7.56 | 2.19 | 9.56 | 7.44 | 2.16 | 9.42
| 2034 | 53 | 2% | 11.92 | 2.7% | 64.9 | 2.1% | 7.66 | 2.24 | 9.7 | 7.55 | 2.21 | 9.55

## Appendix 2
Appendix 2: Capacity Auction Results
Table A2.1 Capacity auction results
| Auction | Date | Awarded Capacity (MW De-Rated)
| 2018/2019 T-1 | 2017-12-15 | 7774
| 2019/2020 T-1 | 2018-12-13 | 8266
| 2020/2021 T-1 | 2019-11-26 | 7606
| 2021/2022 T-2 | 2019-12-05 | 7512
| 2022/2023 T-4 | 2019-03-28 | 7412
| 2022/2023 T-1 | 2020-04-27 | 1121
| 2023/2024 T-4 | 2021-01-21 | 7322
| 2023/2024 T-4 | 2023-09-07 | 639
| 2024/2025 T-4 | 2021-10-21 | 6168
| 2024/2025 T-3 | 2022-01-20 | 1471
| 2025/2026 T-4 | 2022-03-24 | 6484
| 2026/2027 T-4 | 2023-05-04 | 7204
| 2027/2028 T-4 | 2023-12-05 | 5470
| 2024/2025 T-1* | 2024-05-08 | 785
* Provisional results at the time of the data freeze date
Table A2.2 Terminated awarded new capacity
| Technology Class | Terminated Awarded New Capacity (MW)
| Demand Side Unit | 154.903
| Gas Turbine | 1145.005
| Other Storage | 119.64
| Wind | 48.251

## Appendix 3
Appendix 3: Generation Plant Information
Ireland
Table A3.1 Registered capacity of dispatchable generation and interconnectors in Ireland in 2025 (MW)
|  | ID | Fuel Type | Technology Category | 2025 | Comment
| Aghada | AT1 | Gas/DO | Gas Turbine | 90
|  | AT2 | Gas/DO | Gas Turbine | 90
|  | AT4 | Gas/DO | Gas Turbine | 90
|  | AD2 | Gas/DO | Gas Turbine | 449
| All DSU | DSU | DSU | DSU | 830
| Ardnacrusha | AA1-4 | Hydro | Hydro | 86
| Dublin Bay | DB1 | Gas/DO | Gas Turbine | 415
| Dublin Waste | DW1 | Waste | Steam Turbine | 61
| Edenderry | ED1 | Milled peat/ Biomass | Steam Turbine | 118
|  | ED3 | DO/Gas | Gas Turbine | 58
|  | ED5 | DO/Gas | Gas Turbine | 58
| Erne | ER1-4 | Hydro | Hydro | 65
| EWIC | EW1 |  | DC Interconnector | 500
| Great Island CCGT | GI4 | Gas/DO | Gas Turbine | 464
| Huntstown | HNC | Gas/DO | Gas Turbine | 337
|  | HN2 | Gas/DO | Gas Turbine | 408
| Indaver Waste | IW1 | Waste | Steam Turbine | 17
| Lee | LE1-4 | Hydro | Hydro | 27
| Liffey | LI1-4 | Hydro | Hydro | 38
| Moneypoint | MP1 | Coal/HFO | Steam Turbine | 250 | Modelled as not available from the start of July 2025
|  | MP2 | HFO | Steam Turbine | 250 | Modelled as not available from the start of July 2025
|  | MP3 | Coal/HFO | Steam Turbine | 250 | Modelled as not available from the start of July 2025
| Poolbeg CC | PBA | Gas/DO | Gas Turbine | 234
|  | PBB |  | Gas Turbine | 234
| Rhode | RP1 | DO | Gas Turbine | 52
|  | RP2 | DO | Gas Turbine | 52
| Sealrock | SK3 | Gas/DO | Gas Turbine | 81
|  | SK4 | Gas/DO | Gas Turbine | 81
| Tawnaghmore | TP1 | DO | Gas Turbine | 52
|  | TP3 | DO | Gas Turbine | 52
| Turlough Hill | TH1 | Pumped storage | Storage | 292
| Tynagh | TYC | Gas/DO | Gas Turbine | 389
| Whitegate | WG1 | Gas/DO | Gas Turbine | 450
| Total: |  |  |  | 6920
Table A3.2 All renewable energy sources in Ireland (MW)
| At year end: | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Wind Onshore | 5418 | 5744 | 6068 | 6441 | 6811 | 7130 | 7533 | 7939 | 8350 | 8770
| Wind Offshore | 25 | 25 | 25 | 25 | 25 | 1354 | 1952 | 2516 | 3118 | 3727
| Solar PV | 2507 | 3261 | 4014 | 4768 | 5521 | 6279 | 6883 | 7476 | 8061 | 8639
| Small Scale Hydro | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
| Biomass and Biogas | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| Biomass CHP | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
| Industrial | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
| Conventional CHP | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129
| Total | 8168 | 9248 | 10325 | 11452 | 12575 | 14981 | 16586 | 18149 | 19747 | 21354
Northern Ireland
Table A3.3 Registered capacity of dispatchable generation and interconnectors in Northern Ireland in 2025 (MW)
|  | ID | Fuel Type | Technology Category | 2025 | Comment
| Ballylumford | 2025: B31; 2026: Gas/Heavy Fuel Oil; 2027: Gas Turbine; 2028: 246
|  | B32 | Gas/Heavy Fuel Oil | Gas Turbine | 246
|  | B10 | Gas/Heavy Fuel Oil | Gas Turbine | 101
|  | GT7(GT1) | Distillate Oil | Gas Turbine | 58
|  | GT8(GT2) | Distillate Oil | Gas Turbine | 58
| Kilroot | 2025: KGT1; 2026: Distillate Oil; 2027: Gas Turbine; 2028: 29
|  | KGT2 | Distillate Oil | Gas Turbine | 29
|  | KGT3 | Distillate Oil | Gas Turbine | 42
|  | KGT4 | Distillate Oil | Gas Turbine | 42
|  | KGT6 | Gas | Gas Turbine | 350
|  | KGT7 | Gas | Gas Turbine | 350
| Coolkeeragh | 2025: GT8; 2026: Distillate Oil; 2027: Gas Turbine; 2028: 53
|  | C30 | Gas/Distillate Oil | Gas Turbine | 408
| AGU | 2025: AGU; 2026: Distillate Oil; 2027: Gas Turbine; 2028: 79
| DSU | 2025: DSU; 2026: Various; 2027: DSU; 2028: 200
| Lisahally | 2026: Biomass; 2028: 18; 2029: Not in Capacity Market, but assumed available for capacity requirement
| Contour Global | 2025: CGA / CGC; 2026: Gas; 2027: Gas Turbine; 2028: 12
| Moyle | 2027: DC Interconnector; 2028: 450; 2029: Assumed to increase to 500 MW in 2028
| Total: | 2028: 2771
Table A3.4 Partially/Non-Dispatchable plant in Northern Ireland (MW)
| At year end: | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Large Scale Wind | 1255 | 1305 | 1355 | 1455 | 1630 | 2305 | 2480 | 2655 | 2830 | 3005
| Small Scale Wind | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
| Solar PV | 250 | 300 | 350 | 400 | 450 | 500 | 550 | 600 | 650 | 700
| Small Scale Biogas | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| Landfill Gas | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
| Small Scale Biomass | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Renewable CHP | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Other CHP | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Small Scale Hydro | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Waste-to-Energy | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
| Total | 1761 | 1861 | 1961 | 2111 | 2336 | 3061 | 3286 | 3511 | 3736 | 3961
Table A3.5 All renewable energy sources in Northern Ireland (MW)
| At year end: | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| All Wind | 1435 | 1485 | 1535 | 1635 | 1810 | 2485 | 2660 | 2835 | 3010 | 3185
| Solar PV | 250 | 300 | 350 | 400 | 450 | 500 | 550 | 600 | 650 | 700
| All Biomass/Biogas/LFGas/WTE | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
| Renewable CHP | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Hydro | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Total RES | 1773 | 1873 | 1973 | 2123 | 2348 | 3073 | 3298 | 3523 | 3748 | 3973

## Appendix 4
Appendix 4: Alignment of Plexos and AdCal
Figure A4.1 Results of adequacy alignment for Ireland given in MW in terms of surplus (+) and deficit (-) of perfect plant
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| AdCal | -1200 | -1250 | -820 | -740 | -810 | -870 | -960 | -1070
| MW Secure | -1050 | -1180 | -880 | -650 | -690 | -630 | -730 | -800
Table A4.1 Results of adequacy alignment for Ireland given in MW in terms of surplus (+) and deficit (-) of perfect plant
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| AdCal | -1200 | -1250 | -820 | -740 | -810 | -870 | -960 | -1070
| MW Secure | -1050 | -1180 | -880 | -650 | -690 | -630 | -730 | -800
Figure A4.2 Results of adequacy alignment for Northern Ireland given in MW in terms of surplus (+) and deficit (-) of perfect plant
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| AdCal | -170 | -200 | -280 | -280 | -300 | -310 | -320 | -370
| MW Secure | -50 | -100 | -110 | -110 | -120 | -90 | -140 | -190
Figure A4.2 Results of adequacy alignment for Northern Ireland given in MW in terms of surplus (+) and deficit (-) of perfect plant
|  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032
| AdCal | -170 | -200 | -280 | -280 | -300 | -310 | -320 | -370
| MW Secure | -50 | -100 | -110 | -110 | -120 | -90 | -140 | -190

## System Inputs - IE
Ireland Modelling Inputs
Ireland demand
|  |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| NRAA24 Median Transmission Peak Demand (MW) |  | 6019.7669 | 6210.6137 | 6347.0493 | 6456.0135 | 6527.2062 | 6608.1245 | 6713.208 | 6806.8691 | 6914.9829 | 7010.9674
| Reserve Requirement (MW) |  | 375 | 375 | 525 | 525 | 525 | 525 | 525 | 525 | 525 | 525
| Transmission Outage Planning (MW) |  | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350
| Total (MW) |  | 6744.7669 | 6935.6137 | 7222.0493 | 7331.0135 | 7402.2062 | 7483.1245 | 7588.208 | 7681.8691 | 7789.9829 | 7885.9674
Ireland generation portfolio unit capacities
The modelling of the system’s ability to meet the fluctuating demand is a complex function of combined probabilities of forced outage rates, optimisation of scheduled outage, annual run hour limitations and storage capacity and duration. As such, a simple comparison of the demand and total capacities here is not indicative of the adequacy position. The rated capacities and availabilities below are the inputs provided into that complex function.
Rated Capacity (MW)
| Plant Name | ID | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Aghada | AT1 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | AT2 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | AT4 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
|  | AD2 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449 | 449
| Ardnacrusha | AA1 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  | AA2 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  | AA3 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
|  | AA4 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| Dublin Bay | DB1 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415 | 415
| Dublin Waste | DW1 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
| Edenderry | ED1 | 118 | 118 | 118 | 118 | 118 | 118 | 0 | 0 | 0 | 0
|  | ED3 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
|  | ED5 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
| Erne | ER1 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | ER2 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
|  | ER3 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
|  | ER4 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
| Great Island CCGT | GI4 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464 | 464
| Huntstown | HNC | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336
|  | HN2 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408
| Indaver Waste | IW1 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
| Lee | LE1 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
|  | LE2 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  | LE3 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
| Liffey | LI1 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
|  | LI2 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
|  | LI3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  | LI4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Moneypoint | MP1 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | MP2 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | MP3 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Poolbeg CC | PBA | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234
|  | PBB | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234
| Rhode | RP1 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
|  | RP2 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
| Sealrock | SK3 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
|  | SK4 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81
| Tawnaghmore | TP1 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
|  | TP3 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
| Tynagh | TYC | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389
| Whitegate | WG1 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450 | 450
Note: MP1-3 units included as in-market capacity until end of June 2025
New In-Market conventional generation portfolio
Cumulative Rated Capacity (MW)
|  | Plant Name | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
|  | Gas Turbine Auction Results [1] | 1100 | 1210 | 2480 | 2540 | 2540 | 2540 | 2540 | 2540 | 2540 | 2540
|  | Gas Turbine Auction Risk Adjusted Delivery | 530 | 820 | 1570 | 1630 | 1630 | 1630 | 1630 | 1630 | 1630 | 1630
[1] Total capacity from approved capacity auction results which has not been issued with a termination notice.
Note: Values rounded to the nearest 10 MW.
Energy storage portfolio
|  | Type | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
|  | Rated Capacity (MW) | 1100 | 1150 | 1290 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370 | 1370
|  | Energy Storage (MWh) | 2620 | 2700 | 3210 | 3330 | 3330 | 3330 | 3330 | 3330 | 3330 | 3330
Note: Values rounded to the nearest 10 MW.
Demand Side Unit portfolio
|  | Type | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
|  | Rated Capacity (MW) | 830 | 690 | 720 | 860 | 860 | 860 | 860 | 860 | 860 | 860
Note: Capacity values rounded to the nearest 10 MW.
Interconnection portfolio
Net Transfer Capacity (MW) [2]
|  | Unit | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Import | EWIC | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
|  | Greenlink [3] | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
|  | Celtic [3] | 0 | 0 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700
|  | North - South [4] | 300 | 300 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200
| Export | EWIC | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
|  | Greenlink [3] | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
|  | Celtic [3] | 0 | 0 | 700 | 700 | 700 | 700 | 700 | 700 | 700 | 700
|  | North - South [4] | 300 | 300 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250
[2] Rated transfer capacity to be used in economic dispatch model.
[3] Interconnector has not yet been commissioned.
[4] New North South included for the All-Island assessment only. Please refer to post data freeze date changes section in the main report for updated information.
Ireland generation portfolio wind and solar capacities
Rated Capacity (MW)
|  |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
|  | Offshore Wind | 30 | 30 | 30 | 30 | 30 | 1350 | 1950 | 2520 | 3120 | 3730
|  | Onshore Wind | 5420 | 5740 | 6070 | 6440 | 6810 | 7130 | 7530 | 7940 | 8350 | 8770
|  | Solar | 2510 | 3260 | 4010 | 4770 | 5520 | 6280 | 6880 | 7480 | 8060 | 8640
|  | Hydro | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
Other RES / other non-RES portfolio
Rated Capacity (MW)
|  | Type | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Industrial | INDU | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
| Small Scale Hydro | SSH | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
| Conventional CHP | CHP | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129
| Landfill Gas | LFG | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| CHP_Bio | CHP Bio | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
All-island availability statistics
| Technology Category | FOR (%) | Rated Capacity (MW) 2025: SOD (hours); Rated Capacity (MW) 2026: Annual Avail (%)
| DSU | - | Rated Capacity (MW) 2025: -; Rated Capacity (MW) 2026: 28.4
| DSU Run Hour Limited | - | Rated Capacity (MW) 2025: -; Rated Capacity (MW) 2026: 28.2
| Gas Turbine | 8.9 | Rated Capacity (MW) 2025: 470; Rated Capacity (MW) 2026: 85.8
| Hydro | 10.9 | Rated Capacity (MW) 2025: 470; Rated Capacity (MW) 2026: 83.7
| Steam Turbine | 11.3 | Rated Capacity (MW) 2025: 820; Rated Capacity (MW) 2026: 79.3
| Interconnector* | 4.5 | Rated Capacity (MW) 2025: 340; Rated Capacity (MW) 2026: 91.7
| Pumped Hydro Storage | 2.7 | Rated Capacity (MW) 2025: 650; Rated Capacity (MW) 2026: 89.9
| System Wide | 19.2 | Rated Capacity (MW) 2025: 680; Rated Capacity (MW) 2026: 73.1
* Statistics provided by the Regulatory Authorities
Note: The statistics in the table above are reflective of 2019-2023 data.

## System Inputs - NI
Northern Ireland Modelling Inputs
Northern Ireland demand
|  |  | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| NRAA24 Median Transmission Peak Demand (MW) |  | 1570 | 1630 | 1710 | 1760 | 1800 | 1840 | 1880 | 1910 | 1960 | 2000
| Reserve Requirement (MW) |  | 125 | 125 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175
| Total (MW) |  | 1770 | 1830 | 1910 | 1960 | 2000 | 2040 | 2080 | 2110 | 2160 | 2200
Northern Ireland generation portfolio unit capacities
The modelling of the system’s ability to meet the fluctuating demand is a complex function of combined probabilities of forced outage rates, optimisation of scheduled outage, annual run hour limitations and storage capacity and duration. As such, a simple comparison of the demand and total capacities here is not indicative of the adequacy position. The rated capacities and availabilities below are the inputs provided into that complex function.
Rated Capacity (MW)
| Plant Name | ID | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| AGU | AGU | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
| Contour Global | CGA / CGC | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
| Coolkeeragh | GT8 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53
|  | C30 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408 | 408
| Ballylumford | B31 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246
|  | B32 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246
|  | B10 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101
|  | GT7(GT1) | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
|  | GT8(GT2) | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
| Kilroot | KGT1 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
|  | KGT2 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
|  | KGT3 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
|  | KGT4 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
|  | KGT6 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350
|  | KGT7 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350
| Lisahally | Lisahally | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
Energy storage portfolio
|  | Type | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
|  | Rated Capacity (MW) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
|  | Energy Storage (MWh) | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140
Note: Values rounded to the nearest 10 MW.
Demand Side Unit portfolio
|  | Type | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
|  | Rated Capacity (MW) | 200 | 220 | 130 | 170 | 170 | 170 | 170 | 170 | 170 | 170
Note: Capacity values rounded to the nearest 10 MW.
Interconnection portfolio
Net Transfer Capacity (MW) [1]
|  | Unit | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Import | Moyle | 450 | 450 | 450 | 500 | 500 | 500 | 500 | 500 | 500 | 500
|  | North - South [2] | 300 | 300 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250 | 1250
| Export | Moyle | 400 | 400 | 400 | 500 | 500 | 500 | 500 | 500 | 500 | 500
|  | North - South [2] | 300 | 300 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200 | 1200
[1] Rated transfer capacity to be used in economic dispatch model.
[2] New North South included for the All-Island assessment only. Please refer to post data freeze date changes section in the main report for updated information.
Wind and solar portfolio
Rated Capacity (MW)
|  | Source | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
|  | Offshore Wind | 0 | 0 | 0 | 0 | 0 | 500 | 500 | 500 | 500 | 500
|  | Onshore Wind | 1440 | 1490 | 1540 | 1640 | 1810 | 1990 | 2160 | 2340 | 2510 | 2690
|  | Solar | 250 | 300 | 350 | 400 | 450 | 500 | 550 | 600 | 650 | 700
Note: Capacity values rounded to the nearest 10 MW.
Other RES / other non-RES portfolio
Rated Capacity (MW)
|  | Type | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| CHP | NI_CHP | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Biogas | NI_BIOGAS | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
| Biomass | NI_BIOMASS | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Renewable CHP | NI_CHP_RES | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| Hydro | NI_SSH | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
| Landfill Gas | NI_LFG | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
| Diesel | NI_DIESEL | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
All-island availability statistics
| Technology Category | FOR (%) | 2025: SOD (hours); 2026: Annual Avail (%)
| DSU | - | 2025: -; 2026: 28.4
| DSU Run Hour Limited | - | 2025: -; 2026: 28.2
| Gas Turbine | 8.9 | 2025: 470; 2026: 85.8
| Hydro | 10.9 | 2025: 470; 2026: 83.7
| Steam Turbine | 11.3 | 2025: 820; 2026: 79.3
| Interconnector* | 4.5 | 2025: 340; 2026: 91.7
| Pumped Hydro Storage | 2.7 | 2025: 650; 2026: 89.9
| System Wide | 19.2 | 2025: 680; 2026: 73.1
* Statistics provided by the Regulatory Authorities
Note: The statistics in the table above are reflective of 2019-2023 data.